## Tulemused
Projekti nimetus: | Näiteks: Tõravere soojatorustiku rekonstrueerimine
1. | Soojustorustiku renoveerimine ja lokaalkütet kasutava hoone tarbijapaigaldise ühendamine olemasoleva kaugküttevõrguga (määruse § 5 lõike 1 punktides 1 ja 3 nimetatud tegevuste elluviimiseks koostatud projekt) | [5 empty] | Max punktid
1.1 | Projekti tulemusena renoveeritavas soojustorustiku lõigus kokkuhoitud aastane soojusenergia võrreldes eelnenud aasta andmetega | 72.9968 | % | <50% | 50-70% | >70% | 30
1.2 | Aastas kokku hoitavate kasvuhoonegaaside kogus süsinikdioksiidi ekvivalenttonnides, võrreldes taotluse esitamisele eelnenud aasta andmetega | 28.7949 | t CO2e / aastas | Projektide punktid kujunevad pingerea alusel, kusjuures kõige suuremat kokkuhoidu saavutav projekt saab maksimumpunktid ja kõige vähem kokkuhoidnud projekt saab 0 punkti. |  |  | 20
2. | Soojuse tootmise seadme renoveerimine (määruse § 5 lõike 1 punktis 2 nimetatud tegevuse elluviimiseks koostatud projekt)
2.1 | Aastas kokku hoitavate kasvuhoonegaaside heitkogus süsinikdioksiidi ekvivalenttonnides renoveeritava või uue ehitatava soojuse tootmise seadme kohta võrreldes taotluse esitamisele eelnenud aasta andmetega | 0 | t CO2e / aastas | Projektide punktid kujunevad pingerea alusel, kusjuures kõige suurema näitaja saavutav projekt saab maksumumpunktid ja kõige väiksema näitajaga projekt saab 0 punkti. |  |  | 25
| Aastane energia kokkuhoid soojuse tootmisel | 0 | MWh/aastas
2.8 | Soojusjaama efektiivsus | 0.96 | - | ≤1,3 | - | >1,3 | 10 | Arvutatud kogu tootmisjaama prognoositav kasutegur või soojustegur peale projekti elluviimist.
| Summaarne energia kokkuhoid (koos torustiku renoveerimisega) | 439.28 | MWh/aastas
| Taastuvenergia täiendav kasutuselevõtt | 0 | MWh/aastas
| Muu kaasneva õhuheide muutus | 0 | t/aastas

## CO2 arvutus
Taotleja täidab kollased lahtrid!
Projekti nimetus: | Näiteks: Tõravere soojatorustiku rekonstrueerimine
Valida loendist missugusele küttelahendusele minnakse üle |  | Kui soojustootmisseadme vahetust ei toimu, jätta lahter tühjaks
Kaugkütte pakkuja | SW Energia | [12 empty] | https://kotkas.envir.ee/permits/public_index
Soojustootmisjaama nimi | Tõravere katlamaja
Keskkonnaloa nr | L.ÕV.TM-43364 |  |  |  |  | Aastaaruande saab otsida keskonnaloa numbri ja aasta järgi andmebaasist KOTKAS. Kopeeri vajalikud andmed läbipaistvuse suurendamiseks lehele Katlamaja. Kui arunaded KOTKASes katavad vaid osa aastaid, lisada omalt poolt puudvad andmed lehel katlamajad.
Kasutatud aastaaruanne | 2018 - 2020 | [12 empty] | https://kotkas.envir.ee/annual_reports_registry
Kasutatud aastaaruanne viide | https://kotkas.envir.ee/annual_reports_registry/view?search=1&nav_tab=annual_reports_registry&s__permit_nr_like=L.%C3%95V.TM-43364&s__owner_name=&s__year=2020&annual_report_id=24575
Soojustootmisjaama aadress | Torni tn 1, Tõravere alevik, Nõo vald, Tartu maakond
| Enne projekti | Peale projekti
Soojustootmisjaama poolt aastas keskmine toodetav väljundsoojuse kogus | 31802.2518 | 35917.8374 | MWh/aastas | Arvutada taotlusele eelnenud aasta põhjal arvestades vajadusel ka suitsugaaside pesuri poolt tagastatavat soojust; prognoos teha taotluse esitamise aastale eelnenud aasta tegeliku tarbimise põhjal arvestades prognoositavaid muudatusi tarbimises, soojusseadme võimsuses, kasutegris ja kasutatava kütuse kütteväärtuses; vastav seletus peab olema ära toodud ka finantsmajandusanalüüsis ja numbriliselt kajastuma siinses arvutuskäigus. Kui muudatusi soojustootmisseadmes pole planeeritud, siis märkida mõlemasse tabelisse siin ja all samad andmed, st taotluse esitamisele eelnenud aasta väärtus.
Soojusjaama efektiivsus | 0.85 | 0.96 | -
SOOJUSTORUSTIKU PROJEKT
Renoveeritava torustiku pikkus rekonstrueerimise järel | 836.6 | m | Mõeldud on torustiku osa, mis välja vahetatakse, täiendavalt rajatav uus torustik märkida järgmisse lahtrisse.
Uue paigaldatava torustiku pikkus | 0 | m | Mõeldud on vaid täiesti uut rajatavat torustikku, vana torustiku rekonstrueerimist siia mitte arvestada.
Varasem keskmine soojuskadu renoveeritavas torustikus | 601.78 | MWh/aastas | Märkida vaid juba olemasoleva renoveeritava torustiku soojuskadu, uut rajatavat torustikku mitte arvestada!
Prognoositav keskmine soojuskadu renoveeritavas torustikus peale renoveerimist | 162.5 | MWh/aastas | Märkida vaid projekti tulemusel renoveeritava torustiku prognoositav soojuskadu, uut rajatavat torustikku mitte arvestada!
Prognoositav soojuskao vähenemine renoveeritavas torustikus | 439.28 | MWh/aastas
Prognoositav soojuskao vähenemine renoveeritavas torustikus, % | 72.9968 | %
Prognoositav kasvuhoonegaaside heite vähenemine renoveeritavas torustikus eelmise aasta väärtuse alusel | 28.7949 | t CO2e / aastas | Tulemuse saamiseks sisestada allolevasse kahte tabelisse nii taotlusele eelnenud aasta kui prognoositav energiatootmine. Juhul kui soojustootmises muudatusi ei toimu, sisestada mõlemasse tabelisse samad, taotlusele eelnenud aasta andmed.
Prognoositav kasvuhoonegaaside heite vähenemine renoveeritavas torustikus, kui soojustootmises on planeeritud muudatused | 25.4955 | t CO2e / aastas | Tulemuse saamiseks sisestada allolevasse kahte tabelisse nii taotlusele eelnenud aasta kui prognoositav energiatootmine. Juhul kui soojustootmises muudatusi ei toimu, sisestada mõlemasse tabelisse samad, taotlusele eelnenud aasta andmed.
Lisada eelnevalt kasutatud kütuste kogused liigiti (kollased lahtrid) - eelnev tarbimine (taotlusele eelnenud aasta põhjal arvutatuna) iga kütuse liigi kohta eraldi (t/aastas).
Kütuse nimetus | Kasutatud kütuse kogus | Kütteväärtus | Aastane kütteväärtus | Aastane kütteväärtus | Süsinikuheite faktor | ox C osa | CO2/C | CO2 kogus | CH4 emissiooni-faktor | CH4 kogus | N2O emissiooni-faktor | N2O kogus | CO2e kogus* | NOx emissiooni-faktor | NOx kogus | CO emissiooni-faktor | CO kogus | NMVOC emissiooni-faktor | NMVOC kogus | SOx emissiooni-faktor | SOx kogus | TSP emissiooni-faktor | TSP kogus | Muu kaasnev õhuheide kokku
Massiühikutes | t/aasta | MJ/kg | TJ/aasta | GJ/aasta | tC/TJ | arv | 44/12 | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/aasta
LPG | 0 | 45.5 | 0 | 0 | 17.73 | 0.995 | 3.6667 | 0 | 5 | 0 | 0.1 | 0 | 0 | 35.3 | 0 | 418.1 | 0 | 6.1 | 0 | 0.281 | 0 | 15.85 | 0 | 0
Kivisüsi | 0 | 22 | 0 | 0 | 25.74 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 199.42 | 0 | 5.25 | 0 | 0.375 | 0 | 820 | 0 | 19.558 | 0 | 0
Kerge kütteõli | 0 | 42.5 | 0 | 0 | 20.26 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 37 | 0 | 2.2 | 0 | 0.74 | 0 | 46.5 | 0 | 1 | 0 | 0
Masuut | 0 | 40.15 | 0 | 0 | 20.92 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 89 | 0 | 2.6 | 0 | 89 | 0 | 820 | 0 | 0.89 | 0 | 0
Põlevkivi | 0 | 8.16 | 0 | 0 | 26.835 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 79.02 | 0 | 0.88 | 0 | 0 | 0 | 820 | 0 | 429.5 | 0 | 0
Põlevkiviõli (raskem) | 324.75 | 39.22 | 12.7367 | 12736.695 | 21.1 | 0.99 | 3.6667 | 975.5417 | 10 | 127.3669 | 0.6 | 7.642 | 981.0032 | 79.02 | 1006.4536 | 0.88 | 11.2083 | 0 | 0 | 820 | 10444.0899 | 1.9 | 24.1997 | 11485.9516
Põlevkiviõli (kergem) | 0 | 42.3 | 0 | 0 | 20.2 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 79.02 | 0 | 0.88 | 0 | 0 | 0 | 820 | 0 | 1.9 | 0 | 0
Diisel | 0 | 42.3 | 0 | 0 | 19.87 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 250 | 0 | 2.6 | 0 | 89 | 0 | 495 | 0 | 0.89 | 0 | 0
Koksiahjukoks | 0 | 28.5 | 0 | 0 | 29.02 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 199.42 | 0 | 5.25 | 0 | 0.375 | 0 | 820 | 0 | 19.558 | 0 | 0
Õlijäägid | 0 | 16 | 0 | 0 | 20.18 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 37 | 0 | 2.2 | 0 | 0.74 | 0 | 495 | 0 | 1 | 0 | 0
Turvas (turbaplokk) | 0 | 12 | 0 | 0 | 27.82 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.4 | 0 | 0 | 300 | 0 | 4696.75 | 0 | 100 | 0 | 10.8 | 0 | 477.75 | 0 | 0
Turbabrikett | 0 | 16 | 0 | 0 | 26.45 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.4 | 0 | 0 | 300 | 0 | 4696.75 | 0 | 100 | 0 | 10.8 | 0 | 477.75 | 0 | 0
Freesturvas | 0 | 9.7 | 0 | 0 | 28.9 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.4 | 0 | 0 | 300 | 0 | 4696.75 | 0 | 100 | 0 | 10.8 | 0 | 477.75 | 0 | 0
Õlijäägid biojäätmetest | 0 | 16 | 0 | 0 | 20.18 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 37 | 0 | 2.2 | 0 | 0.74 | 0 | 10.8 | 0 | 1 | 0 | 0
Halupuit (niiskussisaldus2 ≤20%) | 0 | 14.76 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Puitbrikett (niiskussisaldus2 ≤12%) | 0 | 16.56 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Puitpellet (niiskussisaldus2 ≤12%) | 0 | 16.56 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Puiduhake, t | 13721.68 | 8.8615 | 121.5952 | 121595.1951 | 30.5 | 1 | 3.6667 | 13598.396 | 300 | 36478.5585 | 4 | 486.3808 | 1056.9054 | 0.736 | 89.4941 | 11.7 | 1422.6638 | 2.2 | 267.5094 | 10.8 | 1313.2281 | 8.7 | 1057.8782 | 4150.7736
Biomass | 0 | 11.9 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 81 | 0 | 90 | 0 | 7.31 | 0 | 10.8 | 0 | 172 | 0 | 0
ruumiühikutes gaas | tuh. m3/aasta | MJ/m3 | TJ/aasta | GJ/aasta | tC/TJ | arv | 44/12 | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/aasta
Maagaas | 0 | 33.6 | 0 | 0 | 15.3 | 0.995 | 3.6667 | 0 | 5 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
Poolkoksigaas | 0 | 43.96 | 0 | 0 | 18.44 | 0.995 | 3.6667 | 0 | 1 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
Generaatorgaas | 0 | 3.4 | 0 | 0 | 42.61 | 0.995 | 3.6667 | 0 | 1 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
Biogaas (prügila- ja reoveesette gaas) | 0 | 17.4 | 0 | 0 | 14.89 | 0.995 | 3.6667 | 0 | 5 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
ruumiühikutes puit | m3/aasta | MJ/m3 | TJ/aasta | GJ/aasta | tC/TJ | arv | 44/12 | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/aasta
Küttepuud, segapuit (ruumimeeter) | 0 | 4680 | 0 | 0 | 30.5 | 0.995 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 |  | 0 | 8.7 | 0 | 0
Küttepuud, kask (ruumimeeter) | 0 | 5400 | 0 | 0 | 30.5 | 0.995 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 |  | 0 | 8.7 | 0 | 0
Puiduhake (puistekuupmeeter) | 0 | 2880 | 0 | 0 | 30.5 | 0.995 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Elekter | Kasutatud kütuse kogus | Kasutatud kütuse kogus | Aastane kütteväärtus | Aastane kütteväärtus |  |  | CO2 emisiooni-faktor | CO2 kogus | CH4 emissiooni-faktor | CH4 kogus | N2O emissiooni-faktor | N2O kogus | CO2e kogus*
| kWh/a | MJ/a | TJ/aasta | GJ/aasta |  |  | g/kWh | t/aasta | g/kWh | kg/aasta | g/kWh | kg/aasta | t/aasta
Tavaline võrguelekter | 100000 | 360000 | 0.36 | 360 |  |  | 467.35 | 46.735 | NA | 0 | NA | 0 | 46.735
Päritolutunnistusega võrguelekter (taastuvelekter) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kohapeal toodetud taastuvelekter | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kasutatav jääksoojus | kWh/a | MJ/a | TJ/aasta | GJ/aasta |  |  | t/TJ | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta
Summaarne jääksoojus | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KOKKU |  |  | 134.6919 | 134691.8901 |  |  |  | 14620.6727 |  | 36605.9255 |  | 494.0228 | 2084.6436 |  | 1095.9477 |  | 1433.8721 |  | 267.5094 |  | 11757.318 |  | 1082.0779 | 15636.7251
Lokaalne mõju kokku |  |  | 134.3319 | 134331.8901 |  |  |  | 14573.9377 |  | 36605.9255 |  | 494.0228 | 2037.9086 |  | 1095.9477 |  | 1433.8721 |  | 267.5094 |  | 11757.318 |  | 1082.0779 | 15636.7251
Lisada uue/uute tarbitava(te) kütuse/kütuste kogused liigiti (kollased lahtrid) - järgnev prognoositav aastane kõigi kütuste tarbimine projekti tulemusel tehtud muudatustega seotud soojustootmise seadmes ja allesjäävates seadmetes. Kui soosjustootmises muudatusi ei plaanita, märkida siia samad väärtused, mis ülemisse tabelisse (taotlusele eelnenud aasta tulemuste alusel).
Kütuse nimetus | Kasutatud kütuse kogus | Kütteväärtus | Aastane kütteväärtus | Aastane kütteväärtus | Süsinikuheite faktor | ox C osa | CO2/C | CO2 kogus | CH4 emissiooni-faktor | CH4 kogus | N2O emissiooni-faktor | N2O kogus | CO2e kogus* | NOx emissiooni-faktor | NOx kogus | CO emissiooni-faktor | CO kogus | NMVOC emissiooni-faktor | NMVOC kogus | SOx emissiooni-faktor | SOx kogus | TSP emissiooni-faktor | TSP kogus | Muu kaasnev õhuheide kokku
Massiühikutes | t/aasta | MJ/kg | TJ/aasta | GJ/aasta | tC/TJ | arv | 44/12 | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/aasta
LPG | 0 | 45.5 | 0 | 0 | 17.73 | 0.995 | 3.6667 | 0 | 5 | 0 | 0.1 | 0 | 0 | 35.3 | 0 | 418.1 | 0 | 6.1 | 0 | 0.281 | 0 | 15.85 | 0 | 0
Kivisüsi | 0 | 22 | 0 | 0 | 25.74 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 199.42 | 0 | 5.25 | 0 | 0.375 | 0 | 820 | 0 | 19.558 | 0 | 0
Kerge kütteõli | 0 | 42.5 | 0 | 0 | 20.26 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 37 | 0 | 2.2 | 0 | 0.74 | 0 | 46.5 | 0 | 1 | 0 | 0
Masuut | 0 | 40.15 | 0 | 0 | 20.92 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 89 | 0 | 2.6 | 0 | 89 | 0 | 820 | 0 | 0.89 | 0 | 0
Põlevkivi | 0 | 8.16 | 0 | 0 | 26.835 | 0.99 | 3.6667 | 0 | 300 | 0 | 0 | 0 | 0 | 79.02 | 0 | 0.88 | 0 | 0 | 0 | 820 | 0 | 429.5 | 0 | 0
Põlevkiviõli (raskem) | 324.75 | 39.22 | 12.7367 | 12736.695 | 21.1 | 0.99 | 3.6667 | 975.5417 | 10 | 127.3669 | 0.6 | 7.642 | 981.0032 | 79.02 | 1006.4536 | 0.88 | 11.2083 | 0 | 0 | 820 | 10444.0899 | 1.9 | 24.1997 | 11485.9516
Põlevkiviõli (kergem) | 0 | 42.3 | 0 | 0 | 20.2 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 79.02 | 0 | 0.88 | 0 | 0 | 0 | 820 | 0 | 1.9 | 0 | 0
Diisel | 0 | 42.3 | 0 | 0 | 19.87 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 250 | 0 | 2.6 | 0 | 89 | 0 | 495 | 0 | 0.89 | 0 | 0
Koksiahjukoks | 0 | 28.5 | 0 | 0 | 29.02 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 199.42 | 0 | 5.25 | 0 | 0.375 | 0 | 820 | 0 | 19.558 | 0 | 0
Õlijäägid | 0 | 16 | 0 | 0 | 20.18 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 37 | 0 | 2.2 | 0 | 0.74 | 0 | 495 | 0 | 1 | 0 | 0
Turvas (turbaplokk) | 0 | 12 | 0 | 0 | 27.82 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 300 | 0 | 4696.75 | 0 | 100 | 0 | 10.8 | 0 | 477.75 | 0 | 0
Turbabrikett | 0 | 16 | 0 | 0 | 26.45 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 300 | 0 | 4696.75 | 0 | 100 | 0 | 10.8 | 0 | 477.75 | 0 | 0
Freesturvas | 0 | 9.7 | 0 | 0 | 28.9 | 0.99 | 3.6667 | 0 | 300 | 0 | 1.5 | 0 | 0 | 300 | 0 | 4696.75 | 0 | 100 | 0 | 10.8 | 0 | 477.75 | 0 | 0
Õlijäägid biojäätmetest | 0 | 16 | 0 | 0 | 20.18 | 0.99 | 3.6667 | 0 | 10 | 0 | 0.6 | 0 | 0 | 37 | 0 | 2.2 | 0 | 0.74 | 0 | 10.8 | 0 | 1 | 0 | 0
Halupuit (niiskussisaldus2 ≤20%) | 0 | 14.76 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Puitbrikett (niiskussisaldus2 ≤12%) | 0 | 16.56 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Puitpellet (niiskussisaldus2 ≤12%) | 0 | 16.56 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Puiduhake | 13721.68 | 8.8615 | 121.5952 | 121595.1951 | 30.5 | 1 | 3.6667 | 13598.396 | 300 | 36478.5585 | 4 | 486.3808 | 1056.9054 | 0.736 | 89.4941 | 11.7 | 1422.6638 | 2.2 | 267.5094 | 10.8 | 1313.2281 | 8.7 | 1057.8782 | 4150.7736
Biomass | 0 | 11.9 | 0 | 0 | 30.5 | 1 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 81 | 0 | 90 | 0 | 7.31 | 0 | 10.8 | 0 | 172 | 0 | 0
ruumiühikutes | tuh. m3/aasta | MJ/m3 | TJ/aasta | GJ/aasta | tC/TJ | arv | 44/12 | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/aasta
Maagaas | 0 | 33.6 | 0 | 0 | 15.3 | 0.995 | 3.6667 | 0 | 5 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
Poolkoksigaas | 0 | 43.96 | 0 | 0 | 18.44 | 0.995 | 3.6667 | 0 | 1 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
Generaatorgaas | 0 | 3.4 | 0 | 0 | 42.61 | 0.995 | 3.6667 | 0 | 1 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
Biogaas (prügila- ja reoveesette gaas) | 0 | 17.4 | 0 | 0 | 14.89 | 0.995 | 3.6667 | 0 | 5 | 0 | 0.1 | 0 | 0 | 89 | 0 | 39.3 | 0 | 2.6 | 0 | 0.281 | 0 | 0.89 | 0 | 0
ruumiühikutes puit | m3/aasta | MJ/m3 | TJ/aasta | GJ/aasta | tC/TJ | arv | 44/12 | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/aasta
Küttepuud, segapuit (ruumimeeter) | 0 | 4680 | 0 | 0 | 30.5 | 0.995 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 |  | 0 | 8.7 | 0 | 0
Küttepuud, kask (ruumimeeter) | 0 | 5400 | 0 | 0 | 30.5 | 0.995 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 |  | 0 | 8.7 | 0 | 0
Puiduhake (puistekuupmeeter) | 0 | 2880 | 0 | 0 | 30.5 | 0.995 | 3.6667 | 0 | 300 | 0 | 4 | 0 | 0 | 0.736 | 0 | 11.7 | 0 | 2.2 | 0 | 10.8 | 0 | 8.7 | 0 | 0
Elekter | Kasutatud kütuse kogus | Kasutatud kütuse kogus | Aastane kütteväärtus | Aastane kütteväärtus |  |  | CO2 emisiooni-faktor | CO2 kogus | CH4 emissiooni-faktor | CH4 kogus | N2O emissiooni-faktor | N2O kogus | CO2e kogus*
| kWh/a | MJ/a | TJ/aasta | GJ/aasta |  |  | g/kWh | t/aasta | g/kWh | kg/aasta | g/kWh | kg/aasta | t/aasta
Tavaline võrguelekter | 100000 | 360000 | 0.36 | 360 |  |  | 467.35 | 46.735 | NA | 0 | NA | 0 | 46.735
Päritolutunnistusega võrguelekter (taastuvelekter) | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kohapeal toodetud taastuvelekter | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kasutatav jääksoojus | kWh/a | MJ/a | TJ/aasta | GJ/aasta |  |  | t/TJ | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta
Summaarne jääksoojus | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KOKKU |  |  | 134.6919 | 134691.8901 |  |  |  | 14620.6727 |  | 36605.9255 |  | 494.0228 | 2084.6436 |  | 1095.9477 |  | 1433.8721 |  | 267.5094 |  | 11757.318 |  | 1082.0779 | 15636.7251
Lokaalne mõju kokku |  |  | 134.3319 | 134331.8901 |  |  |  | 14573.9377 |  | 36605.9255 |  | 494.0228 | 2037.9086 |  | 1095.9477 |  | 1433.8721 |  | 267.5094 |  | 11757.318 |  | 1082.0779 | 15636.7251
[8 empty] | CO2 kogus | CH4 emissiooni-faktor | CH4 kogus | N2O emissiooni-faktor | N2O kogus | CO2e kogus* | NOx emissiooni-faktor | NOx kogus | CO emissiooni-faktor | CO kogus | NMVOC emissiooni-faktor | NMVOC kogus | SOx emissiooni-faktor | SOx kogus | TSP emissiooni-faktor | TSP kogus | Muu kaasnev õhuheide kokku
[8 empty] | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | t/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/TJ | kg/aasta | kg/aasta
Summaarne heite vähenemine soojustootmisseadmes | [7 empty] | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
Lokaalse heite vähenemine soojustootmisseadmes | [7 empty] | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
| TJ/aastas | MWh/aastas
Kütuste summaarne kütteväärtus enne | 134.6919 | 37414.4139
Kütuste summaarne kütteväärtus pärast | 134.6919 | 37414.4139
Aastane energia kokkuhoid soojuse tootmisel | 0 | 0
Soojuse (energia) tootmise kasutegur enne | 0.85 | -
Soojuse (energia) tootmise kasutegur pärast | 0.96 | -
Soojuse (energia) tootmise efektiivsuse suurenemise tulemusel tekkiv energiasääst | 4115.5855 | MWh/aastas | Võrdlusstsenaariumina on kasutatud hüpoteetilist olukorda, kus sama kogus väljundsoojust oleks toodetud eelnevalt kasutusel olnud soojustootmisseadme ja selle eelneva seadistuse abil
Taastuvenergia täiendav kasutuselevõtt | 0 | MWh/aastas | Tulevikus kasutusele võetava aastase taastuvenergia ja varem kasutatud aastase taastuvenergia energiasisalduste vahe
Taastumatu energia kasutuse vähenemine aastas | 0 | MWh/aastas | Tulevikus kasutusel oleva aastase taastumatu energia ja varem kasutatud aastase taastumatu energia energiasisalduste vahe
Summaarne energia kokkuhoid (koos torustiku renoveerimisega) | 439.28 | MWh/aastas
Selgitused
* CO2e = CO2 + 25*CH4 + 298*N2O (t/aastas), on summaarne kavuhoonegaaside heide CO2 ekvivalentides. Arvutuses on arvesse võetud, et atmosfääris on CH4 25 korda ja N2O 298 korda mõjusam kasvuhoonegaas kui CO2. Taastuvate kütuste korral ei arvestata CO2 kasvuhoonegaaside summaarse heite koostisesse, kuna tegemist on looduslikust ringest pärit süsinikuga, arvestatakse vaid CH4 ja N2O heidet.
Värvikoodid tabelites
Biokütused, mille korral ei arvestata CO2 heidet on märgitud heleroheliste tulpadega
Andmed allikast: | EMEP/EEA air pollutant emission inventory guidebook 2019 | [5 empty] | http://efdb.apps.eea.europa.eu/?source=%7B%22query%22%3A%7B%22bool%22%3A%7B%22must%22%3A%7B%22match_all%22%3A%7B%7D%7D%2C%22filter%22%3A%7B%22bool%22%3A%7B%22must%22%3A%5B%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22code%22%3A%221.A.4.b.i%20Residential%20plants%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Pollutant%22%3A%22BC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CH4%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO2%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22N2O%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NH3%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NMVOC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NOx%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM10%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM2.5%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22TSP%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Fuel%22%3A%22%27Other%27%20Liquid%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Biomass%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Coal%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gas%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gaseous%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Hard%20Coal%20and%20Brown%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Natural%20Gas%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Solid%20Fuel%20(not%20biomass)%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%20and%20similar%20wood%20waste%22%7D%7D%5D%7D%7D%5D%7D%7D%7D%7D%2C%22display_type%22%3A%22tabular%22%7D | [9 empty] | Olemas ka lehel "Heited väikesed kütteseadmed EU"
Andmed allikast: | EMEP/EEA air pollutant emission inventory guidebook 2019 | [5 empty] | http://efdb.apps.eea.europa.eu/?source=%7B%22query%22%3A%7B%22bool%22%3A%7B%22must%22%3A%7B%22match_all%22%3A%7B%7D%7D%2C%22filter%22%3A%7B%22bool%22%3A%7B%22must%22%3A%5B%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Pollutant%22%3A%22CH4%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO2%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22N2O%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NH3%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22BC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22Benzo(a)pyrene%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22Benzo(b)fluoranthene%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22Benzo(k)fluoranthene%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NMVOC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NOx%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22HCB%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PCB%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM10%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM2.5%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22SOx%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22TSP%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Fuel%22%3A%22%27Other%27%20Liquid%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Coal%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Hard%20Coal%20and%20Brown%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Solid%20Fuel%20(not%20biomass)%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%20and%20similar%20wood%20waste%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Biomass%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Brown%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Brown%20Coal%2FLignite%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Coking%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gas%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gas%20oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gaseous%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gaseous%20fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Hard%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Heavy%20Fuel%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Natural%20Gas%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Natural%20gas%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Residual%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%20and%20wood%20waste%20(clean%20wood%20waste)%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Steam%20Coal%20%26%20Sub-Bituminous%20Coal%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22code%22%3A%221.A.1.a%20Public%20electricity%20and%20heat%20production%22%7D%7D%5D%7D%7D%5D%7D%7D%7D%7D%2C%22display_type%22%3A%22tabular%22%7D | [9 empty] | Olemas ka lehel "Heited suured kütteseadmed EU"
Valgete lahtrite andmed allikast: |  | GREENHOUSE GAS EMISSIONS IN ESTONIA 1990-2019 NATIONAL INVENTORY REPORT | [7 empty] | https://unfccc.int/sites/default/files/resource/est-2021-nir-15apr21_0.zip | [6 empty] | Olemas ka lehel "Kütteväärtused ja heited EU"
Andmed allikast: | Andmed täpsemalt arvutatud lehel "Elekter 2021"
Ümberarvutus vatt-tundidest kilodžaulideks |  |  |  | Küttepuude teisendus massiühikule |  |  |  |  | GWP - globaalsed soojenemispotensiaalid (võrreldes CO2-ga)
1Wh=3,6kJ | 3.6 |  |  |  | MJ/m3 | MJ/kg |  |  | GWP CH4 | GWP N2O
1kWh=3600kJ=3,6MJ |  |  | Küttepuud, segapuit (ruumimeeter) |  | 4680 | 11.6033 |  |  | 25 | 298
1MWh=1000kWh=3,6GJ=0,0036TJ | 0.0036 | 277.7778 | Küttepuud, kask (ruumimeeter) |  | 5400 | 16.3636
Ühikuteisendus: |  |  | Puiduhake (puistekuupmeeter) |  | 2880 | 8.8615
g/GJ = kg/TJ
Kütuste kütteväärtused saadud allikast: | [6 empty] | Juurde on vaja siis, mis kütusele üle mindi ja kui palju seda kulub (saab arvutada senise soojakulu järgi) ja sealt tekkiv jalajälg kahe vahest.
https://www.riigiteataja.ee/aktilisa/1181/0201/2001/MKM_m63_lisa4.pdf
Projekti tulemusel toimuva muutuse rippmenüü valikud
katla renoveerimine
katla asendus
suitsugaaside pesur/kondensaator
soojuspump
koostootmine
Katlamaja rippmenüü valikud
LPG
Kivisüsi
Kerge kütteõli
Masuut
Põlevkivi
Põlevkiviõli (raskem)
Põlevkiviõli (kergem)
Diisel
Koksiahjukoks
Õlijäägid
Turvas (mättad)
Turbabrikett
Freesturvas
Õlijäägid biojäätmetest
Halupuit (niiskussisaldus2 ≤20%)
Puitbrikett (niiskussisaldus2 ≤12%)
Puitpellet (niiskussisaldus2 ≤12%)
Puiduhake, t
Maagaas
Biogaas (prügila- ja reoveesette gaas)
Küttepuud, segapuit (ruumimeeter)
Küttepuud, kask (ruumimeeter)
Puiduhake (puistekuupmeeter)
NA

## Katlamajad
Kopeeri aruandlusaastast siia vajalikud andmed (lae aruande pdf alla ja ava wordi failina, seejärel kopeeri vajalikud tabelid tervikuna siia)
Viide aruandele |  | https://kotkas.envir.ee/annual_reports_registry/view?search=1&nav_tab=annual_reports_registry&s__permit_nr_like=L.%C3%95V.TM-43364&s__owner_name=&s__year=2020&annual_report_id=24575
2.5. Kütuste ning jäätmete kasutamine ja energia tootmine tegevusalade kaupa
Kasutatav kütus ja jäätmed | [6 empty] | Energia tootmine, MWh/a
Kütuse liik | Kütuse nimetus | KN kood | KN nimetus | Tegevusala või tootmisprotsess |  |  | Elekter |  |  | Soojus ja aur
|  |  |  | SNAP kood | Kütuse ja jäätmete kogus aastas |  | Kokku | Omatarve | Müük | Kokku | Omatarve | Müük
[5 empty] | Kogus | Ühik
Tahke kütus | Puiduhake | 440139 | puiduhake ja puidujäätmed | 010203b - Piirkondlikud katlamajad - põletusseade | 492.7 | tonni | 0 | 0 | 0 | 1058.621 | 0 | 899
< 20 MW (katlad)
Vedelkütus | Põlevkiviõli (raske fraktsioon) | 27101964 | põlevkiviõli | 010203b - Piirkondlikud katlamajad - põletusseade | 3.718 | tonni | 0 | 0 | 0 | 35.321 | 0 | 35.321
< 20 MW (katlad)

## Heited suured kütteseamed EU (hidden)
NFR | Sector | Table | Type | Technology | Fuel | Abatement | Region | Pollutant | Value | Unit | CI_lower | CI_upper | Reference
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | BC | 3.3 | % of PM2.5 | 1.6 | 6.6 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | Benzo(a)pyrene | 1.12 | mg/GJ | 0.671 | 1.57 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | Benzo(b)fluoranthene | 0.043 | mg/GJ | 0.0215 | 0.0645 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | Benzo(k)fluoranthene | 0.0155 | mg/GJ | 0.00774 | 0.0232 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | CO | 90 | g/GJ | 45 | 180 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | HCB | 5 | µg/GJ | 0.5 | 50 | Bailey, 2001
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | NMVOC | 7.31 | g/GJ | 2.44 | 21.9 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | NOx | 81 | g/GJ | 40 | 160 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | PCB | 3.5 | µg/GJ | 0.35 | 35 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | PM10 | 155 | g/GJ | 77 | 310 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | PM2.5 | 133 | g/GJ | 66 | 266 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | SOx | 10.8 | g/GJ | 6.45 | 15.1 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-7 | Tier 1 emission factor | NA | Biomass |  | NA | TSP | 172 | g/GJ | 86 | 344 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | Benzo(a)pyrene | 1.3 | µg/GJ | 0.26 | 6.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | Benzo(a)pyrene | 1.3 | µg/GJ | 0.26 | 6.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | Benzo(b)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | Benzo(b)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | CO | 13 | g/GJ | 0.1 | 26 | European Commission (2006)
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | NMVOC | 1 | g/GJ | 0.2 | 5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | NOx | 60 | g/GJ | 35 | 85.2 | European Commission (2006)
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | PM10 | 6.9 | g/GJ | 2.3 | 20.7 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | PM2.5 | 2.8 | g/GJ | 0.9 | 8.4 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | SOx | 1680 | g/GJ | 330 | 5000 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-16 | Tier 2 emission factor | Fluid Bed Boilers | Brown Coal |  | NA | TSP | 10.2 | g/GJ | 3.4 | 30.6 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | BC | 1 | % of PM2.5 | 0.1 | 4 | Kupiainen and Klimont (2007)
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | Benzo(a)pyrene | 1.3 | µg/GJ | 0.26 | 6.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | Benzo(k)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | CO | 8.7 | g/GJ | 6.72 | 60.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | NMVOC | 1.4 | g/GJ | 0.84 | 3.36 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | NOx | 247 | g/GJ | 143 | 571 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | PCB | 3.3 | ng WHO-TEG/GJ | 1.1 | 9.9 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | PM10 | 7.9 | g/GJ | 1 | 79 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | PM2.5 | 3.2 | g/GJ | 1 | 32 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | SOx | 1680 | g/GJ | 330 | 5000 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-3 | Tier 1 emission factor | NA | Brown Coal |  | NA | TSP | 11.7 | g/GJ | 1.2 | 117 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | Benzo(a)pyrene | 1.3 | µg/GJ | 0.26 | 6.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | Benzo(a)pyrene | 1.3 | µg/GJ | 0.26 | 6.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | Benzo(k)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | Benzo(k)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | CO | 8.7 | g/GJ | 6.72 | 60.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | CO | 8.7 | g/GJ | 6.72 | 60.5 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | NMVOC | 1.4 | g/GJ | 0.84 | 3.36 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | NMVOC | 1.4 | g/GJ | 0.84 | 3.36 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | NOx | 247 | g/GJ | 143 | 571 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | NOx | 247 | g/GJ | 143 | 571 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | PCB | 3.3 | ng WHO-TEG/GJ | 1.1 | 9.9 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | PCB | 3.3 | ng WHO-TEG/GJ | 1.1 | 9.9 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | PM10 | 7.9 | g/GJ | 1 | 79 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | PM10 | 7.9 | g/GJ | 1 | 79 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | PM2.5 | 3.2 | g/GJ | 1 | 32 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | PM2.5 | 3.2 | g/GJ | 1 | 32 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | SOx | 1680 | g/GJ | 330 | 5000 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | SOx | 1680 | g/GJ | 330 | 5000 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | TSP | 11.7 | g/GJ | 1.2 | 117 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-10 | Tier 2 emission factor | Wet and Dry Bottom Boilers | Brown Coal/Lignite |  | NA | TSP | 11.7 | g/GJ | 1.2 | 117 | US EPA (1998), chapter 1.7
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | BC | 2.2 | % of PM2.5 | 0.27 | 8.08 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(a)pyrene | 0.736 | µg/GJ | 0.245 | 2.21 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(a)pyrene | 0.736 | µg/GJ | 0.245 | 2.21 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(k)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(k)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | CO | 8.7 | g/GJ | 6.15 | 15 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | NMVOC | 1 | g/GJ | 0.6 | 2.4 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | NOx | 209 | g/GJ | 200 | 350 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | PCB | 3.3 | ng WHO-TEG/GJ | 1.1 | 9.9 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | PM10 | 7.7 | g/GJ | 2 | 200 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | PM2.5 | 3.4 | g/GJ | 0.9 | 90 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | SOx | 820 | g/GJ | 330 | 5000 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-9 | Tier 2 emission factor | Dry Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | TSP | 11.4 | g/GJ | 3 | 300 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | BC | 2.2 | % of PM2.5 | 0.27 | 8.08 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(a)pyrene | 0.736 | µg/GJ | 0.245 | 2.21 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(b)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | CO | 8.7 | g/GJ | 6.15 | 150 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | NMVOC | 0.7 | g/GJ | 0.4 | 1.6 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | NOx | 244 | g/GJ | 120 | 488 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | PCB | 3.3 | ng WHO-TEQ/GJ | 1.1 | 9.9 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | PM10 | 6 | g/GJ | 6 | 24 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | PM2.5 | 3.1 | g/GJ | 3 | 12 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | SOx | 820 | g/GJ | 330 | 5000 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-14 | Tier 2 emission factor | Wet Bottom Boilers | Coking Coal, Steam Coal & Sub-Bituminous Coal |  | NA | TSP | 8 | g/GJ | 7.5 | 30 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | BC | 33.5 | % of PM2.5 | 28.9 | 38 | Hildemann et al., 1981 & Bond et al., 2006
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | CO | 1.49 | g/GJ | 0.89 | 2.09 | US EPA (2000), chapter 3.1
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | NMVOC | 0.19 | g/GJ | 0.11 | 0.26 | US EPA (2000), chapter 3.1
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | NOx | 398 | g/GJ | 239 | 557 | US EPA (2000), chapter 3.1
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | PM10 | 1.95 | g/GJ | 0.65 | 5.85 | US EPA (2000), chapter 3.1
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | PM2.5 | 1.95 | g/GJ | 0.65 | 5.85 | US EPA (2000), chapter 3.1
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | SOx | 46.5 | g/GJ | 4.65 | 465 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-18 | Tier 2 emission factor | Gas Turbines | Gas Oil |  | NA | TSP | 1.95 | g/GJ | 0.65 | 5.85 | US EPA (2000), chapter 3.1
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | BC | 78 | % of PM2.5 | 63 | 93 | Hernandez et al., 2004
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | Benzo(a)pyrene | 0.116 | mg/GJ | 0.0582 | 0.116 | US EPA (1996), chapter 3.3 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | Benzo(b)fluoranthene | 0.502 | mg/GJ | 0.251 | 0.754 | US EPA (1996), chapter 3.3 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | Benzo(k)fluoranthene | 0.0987 | mg/GJ | 0.0493 | 0.0987 | US EPA (1996), chapter 3.3 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | CO | 130 | g/GJ | 30 | 230 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | HCB | 0.22 | µg/GJ | 0.022 | 2.2 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | NMVOC | 37.1 | g/GJ | 18.5 | 55.6 | US EPA (1996), chapter 3.3
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | NOx | 942 | g/GJ | 500 | 1380 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | PCB | 0.13 | ng I-TEQ/GJ | 0.013 | 1.3 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | PM10 | 22.4 | g/GJ | 11.2 | 44.8 | US EPA (1996), chapter 3.3
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | PM2.5 | 21.7 | g/GJ | 10.8 | 43.4 | US EPA (1996), chapter 3.3
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | SOx | 46.5 | g/GJ | 4.65 | 465 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-19 | Tier 2 emission factor | Large stationary CI reciprocating engines | Gas Oil |  | NA | TSP | 28.1 | g/GJ | 14.1 | 56.2 | US EPA (1996), chapter 3.3
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | BC | 33.5 | % of PM2.5 | 28.9 | 38 | Hildemann et al., 1981 & Bond et al., 2006
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | CO | 16.2 | g/GJ | 4 | 65 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | NMVOC | 0.8 | g/GJ | 0.48 | 1.28 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | NOx | 65 | g/GJ | 22 | 195 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | PM10 | 3.2 | g/GJ | 1 | 10 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | PM2.5 | 0.8 | g/GJ | 0.3 | 2.5 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | SOx | 46.5 | g/GJ | 4.65 | 465 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-6 | Tier 1 emission factor | NA | Gas oil |  | NA | TSP | 6.5 | g/GJ | 2 | 20 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | BC | 2.5 | % of PM2.5 | 1 | 6.3 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | Benzo(a)pyrene | 0.56 | µg/GJ | 0.19 | 0.56 | US EPA (1998), chapter 1.4 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | Benzo(b)fluoranthene | 1.58 | µg/GJ | 0.5 | 4.7 | API, 1998
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | Benzo(k)fluoranthene | 1.11 | µg/GJ | 0.4 | 3.3 | API, 1998
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | CO | 4.8 | g/GJ | 1 | 70 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | NMVOC | 1.6 | g/GJ | 0.5 | 7.6 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | NOx | 153 | g/GJ | 92 | 245 | US EPA (2000), chapter 3.1
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | PM10 | 0.2 | g/GJ | 0.05 | 0.8 | BUWAL, 2001
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | PM2.5 | 0.2 | g/GJ | 0.05 | 0.8 | Assumed equal to PM2.5
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | SOx | 0.281 | g/GJ | 0.169 | 0.393 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-17 | Tier 2 emission factor | Gas Turbines | Gaseous Fuels |  | NA | TSP | 0.2 | g/GJ | 0.05 | 0.8 | BUWAL, 2001
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | BC | 2.5 | % of PM2.5 | 1 | 6.3 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | Benzo(a)pyrene | 0.562 | µg/GJ | 0.187 | 1.69 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | Benzo(b)fluoranthene | 0.843 | µg/GJ | 0.281 | 2.53 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | Benzo(k)fluoranthene | 0.843 | µg/GJ | 0.281 | 2.53 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | CO | 39.3 | g/GJ | 19.7 | 60 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | NMVOC | 2.6 | g/GJ | 0.65 | 10.4 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | NOx | 89 | g/GJ | 15.6 | 180 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | PM10 | 0.89 | g/GJ | 0.445 | 1.33 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | PM2.5 | 0.89 | g/GJ | 0.445 | 1.33 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | SOx | 0.281 | g/GJ | 0.169 | 0.393 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-4 | Tier 1 emission factor | NA | Gaseous fuels |  | NA | TSP | 0.89 | g/GJ | 0.445 | 1.33 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | BC | 2.2 | % of PM2.5 | 0.27 | 8.08 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | Benzo(a)pyrene | 0.736 | µg/GJ | 0.245 | 2.21 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | Benzo(a)pyrene | 0.736 | µg/GJ | 0.245 | 2.21 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | Benzo(b)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | Benzo(b)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | CO | 313 | g/GJ | 150 | 600 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | NMVOC | 0.9 | g/GJ | 0.6 | 2.4 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | NOx | 82.5 | g/GJ | 10 | 112 | European Commission (2006)
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | PCB | 170 | µg/GJ | 85 | 260 | Kakareka et al. (2004)
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | PCB | 170 | µg/GJ | 85 | 260 | Kakareka et al. (2004)
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | PM10 | 7.7 | g/GJ | 6 | 24 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | PM2.5 | 5.2 | g/GJ | 3 | 12 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | SOx | 820 | g/GJ | 330 | 5000 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-15 | Tier 2 emission factor | Fluid Bed Boilers | Hard Coal |  | NA | TSP | 8.4 | g/GJ | 7.5 | 30 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | BC | 2.2 | % of PM2.5 | 0.27 | 8.08 | See Note in Guidebook Chapter
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | Benzo(a)pyrene | 0.74 | µg/GJ | 0.25 | 2.21 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | Benzo(b)fluoranthene | 37 | µg/GJ | 3.7 | 370 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | Benzo(k)fluoranthene | 29 | µg/GJ | 2.9 | 290 | Wenborn et al., 1999
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | CO | 8.7 | g/GJ | 6.15 | 15 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | HCB | 6.7 | µg/GJ | 2.2 | 20.1 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | NMVOC | 1 | g/GJ | 0.6 | 2.4 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | NOx | 209 | g/GJ | 200 | 350 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | PCB | 3.3 | ng WHO-TEG/GJ | 1.1 | 9.9 | Grochowalski & Konieczyński, 2008
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | PM10 | 7.7 | g/GJ | 2 | 200 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | PM2.5 | 3.4 | g/GJ | 0.9 | 90 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | SOx | 820 | g/GJ | 300 | 5000 | See Note in Guidebook Chapter
1.A.1.a | Public electricity and heat production | Table_3-2 | Tier 1 emission factor | NA | Hard Coal |  | NA | TSP | 11.4 | g/GJ | 3 | 300 | US EPA (1998), chapter 1.1
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | BC | 5.6 | % of PM2.5 | 0.22 | 8.69 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | CO | 5 | g/GJ | 3 | 7 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | NMVOC | 0.8 | g/GJ | 0.48 | 1.28 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | NOx | 142 | g/GJ | 70 | 300 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | PM10 | 25.2 | g/GJ | 1.5 | 150 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | PM2.5 | 19.3 | g/GJ | 0.9 | 90 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | SOx | 495 | g/GJ | 146 | 1700 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-5 | Tier 1 emission factor | NA | Heavy Fuel Oil |  | NA | TSP | 35.4 | g/GJ | 2 | 200 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | BC | 2.5 | % of PM2.5 | 1 | 6.3 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | BC | 2.5 | % of PM2.5 | 1 | 6.3 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | Benzo(a)pyrene | 0.56 | µg/GJ | 0.19 | 0.56 | US EPA (1998), chapter 1.4 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | Benzo(a)pyrene | 0.56 | µg/GJ | 0.19 | 0.56 | US EPA (1998), chapter 1.4 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | Benzo(b)fluoranthene | 0.84 | µg/GJ | 0.28 | 0.84 | US EPA (1998), chapter 1.4 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | Benzo(b)fluoranthene | 0.84 | µg/GJ | 0.28 | 0.84 | US EPA (1998), chapter 1.4 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | Benzo(k)fluoranthene | 0.84 | µg/GJ | 0.28 | 0.84 | US EPA (1998), chapter 1.4 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | Benzo(k)fluoranthene | 0.84 | µg/GJ | 0.28 | 0.84 | US EPA (1998), chapter 1.4 ("Less than" value based on method detection limits)
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | CO | 39 | g/GJ | 20 | 60 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | CO | 39 | g/GJ | 20 | 60 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | NMVOC | 2.6 | g/GJ | 0.65 | 10.4 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | NMVOC | 2.6 | g/GJ | 0.65 | 10.4 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | NOx | 89 | g/GJ | 15 | 185 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | NOx | 89 | g/GJ | 15 | 185 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | PM10 | 0.89 | g/GJ | 0.445 | 1.34 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | PM10 | 0.89 | g/GJ | 0.445 | 1.34 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | PM2.5 | 0.89 | g/GJ | 0.445 | 1.34 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | PM2.5 | 0.89 | g/GJ | 0.445 | 1.34 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | SOx | 0.281 | g/GJ | 0.169 | 0.393 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | SOx | 0.281 | g/GJ | 0.169 | 0.393 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | TSP | 0.89 | g/GJ | 0.445 | 1.34 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-12 | Tier 2 emission factor | Dry Bottom Boilers | Natural Gas |  | NA | TSP | 0.89 | g/GJ | 0.445 | 1.34 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | BC | 2.5 | % of PM2.5 | 1 | 6.3 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | Benzo(a)pyrene | 1.2 | µg/GJ | 0.24 | 6 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | Benzo(b)fluoranthene | 9 | µg/GJ | 1.8 | 45 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | Benzo(k)fluoranthene | 1.7 | µg/GJ | 0.34 | 8.5 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | CO | 56 | g/GJ | 20 | 135 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | NMVOC | 89 | g/GJ | 45 | 135 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | NOx | 135 | g/GJ | 65 | 200 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | PM10 | 2 | g/GJ | 1 | 3 | BUWAL, 2001
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | PM2.5 | 2 | g/GJ | 1 | 3 | BUWAL, 2001
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | SOx | 0.281 | g/GJ | 0.169 | 0.393 | US EPA (1998), chapter 1.4
1.A.1.a | Public electricity and heat production | Table_3-20 | Tier 2 emission factor | Stationary reciprocating Engines - gas-fired | Natural gas |  | NA | TSP | 2 | g/GJ | 1 | 3 | BUWAL, 2001
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | BC | 5.6 | % of PM2.5 | 0.22 | 8.69 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | BC | 5.6 | % of PM2.5 | 0.22 | 8.69 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | CO | 15.1 | g/GJ | 9.06 | 21.1 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | CO | 15.1 | g/GJ | 9.06 | 21.1 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | NMVOC | 2.3 | g/GJ | 1.4 | 3.2 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | NMVOC | 2.3 | g/GJ | 1.4 | 3.2 | US EPA (1998), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | NOx | 142 | g/GJ | 70 | 300 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | NOx | 142 | g/GJ | 70 | 300 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | PM10 | 25.2 | g/GJ | 1.5 | 150 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | PM10 | 25.2 | g/GJ | 1.5 | 150 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | PM2.5 | 19.3 | g/GJ | 0.9 | 90 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | PM2.5 | 19.3 | g/GJ | 0.9 | 90 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | SOx | 495 | g/GJ | 146 | 1700 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | SOx | 495 | g/GJ | 146 | 1700 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | TSP | 35.4 | g/GJ | 2 | 200 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-11 | Tier 2 emission factor | Dry Bottom Boilers | Residual Oil |  | NA | TSP | 35.4 | g/GJ | 2 | 200 | US EPA (2010), chapter 1.3
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | BC | 3.3 | % of PM2.5 | 1.6 | 6.6 | See note in Guidebook chapter
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | Benzo(a)pyrene | 1.12 | mg/GJ | 0.671 | 1.57 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | Benzo(a)pyrene | 1.12 | mg/GJ | 0.671 | 1.57 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | Benzo(b)fluoranthene | 0.043 | mg/GJ | 0.0215 | 0.0645 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | Benzo(b)fluoranthene | 0.043 | mg/GJ | 0.0215 | 0.0645 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | Benzo(k)fluoranthene | 0.0155 | mg/GJ | 0.00774 | 0.0232 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | Benzo(k)fluoranthene | 0.0155 | mg/GJ | 0.00774 | 0.0232 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | CO | 90 | g/GJ | 45 | 180 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | HCB | 5 | µg/GJ | 0.5 | 50 | Bailey, 2001
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | NMVOC | 7.31 | g/GJ | 2.44 | 21.9 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | NOx | 81 | g/GJ | 40 | 160 | Nielsen et al., 2010
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | PCB | 3.5 | µg/GJ | 0.35 | 35 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | PM10 | 155 | g/GJ | 77 | 310 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | PM2.5 | 133 | g/GJ | 66 | 266 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | SOx | 10.8 | g/GJ | 6.45 | 15.1 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | SOx | 10.8 | g/GJ | 6.45 | 15.1 | US EPA (2003), chapter 1.6
1.A.1.a | Public electricity and heat production | Table_3-13 | Tier 2 emission factor | Dry Bottom Boilers | Wood and wood waste (clean wood waste) |  | NA | TSP | 172 | g/GJ | 86 | 344 | US EPA (2003), chapter 1.6
Allikas: | http://efdb.apps.eea.europa.eu/?source=%7B%22query%22%3A%7B%22bool%22%3A%7B%22must%22%3A%7B%22match_all%22%3A%7B%7D%7D%2C%22filter%22%3A%7B%22bool%22%3A%7B%22must%22%3A%5B%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Pollutant%22%3A%22CH4%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO2%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22N2O%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NH3%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22BC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22Benzo(a)pyrene%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22Benzo(b)fluoranthene%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22Benzo(k)fluoranthene%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NMVOC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NOx%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22HCB%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PCB%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM10%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM2.5%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22SOx%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22TSP%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Fuel%22%3A%22%27Other%27%20Liquid%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Coal%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Hard%20Coal%20and%20Brown%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Solid%20Fuel%20(not%20biomass)%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%20and%20similar%20wood%20waste%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Biomass%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Brown%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Brown%20Coal%2FLignite%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Coking%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gas%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gas%20oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gaseous%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gaseous%20fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Hard%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Heavy%20Fuel%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Natural%20Gas%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Natural%20gas%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Residual%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%20and%20wood%20waste%20(clean%20wood%20waste)%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Steam%20Coal%20%26%20Sub-Bituminous%20Coal%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22code%22%3A%221.A.1.a%20Public%20electricity%20and%20heat%20production%22%7D%7D%5D%7D%7D%5D%7D%7D%7D%7D%2C%22display_type%22%3A%22tabular%22%7D
Lühendid põlemisel tekkivate lenduvate saasteainete kohta: |  |  |  |  | Nimetus aastaaruannetes
BC | must süsinik, mõõdetakse % PM2.5 suhtes | must süsinik, mõõdetakse % PM2.5 suhtes | must süsinik, mõõdetakse % PM2.5 suhtes |  | -
CO | CO - süsnikmonooksiid | CO - süsnikmonooksiid | CO - süsnikmonooksiid |  | Süsinikmonooksiid
NH3 | NH3 - ammoniaak | NH3 - ammoniaak | NH3 - ammoniaak
NMVOC | lenduvad orgaanilised ained v.a. metaan | lenduvad orgaanilised ained v.a. metaan | lenduvad orgaanilised ained v.a. metaan |  | Lenduvad orgaanilised ühendid kütuse põletamisel
NOx | NOx - lämmastiku oksiidid | NOx - lämmastiku oksiidid | NOx - lämmastiku oksiidid |  | Lämmastikdioksiid
PM10 | PM10 - tahked osakesed suurusega alla 10 mikromeetri | PM10 - tahked osakesed suurusega alla 10 mikromeetri | PM10 - tahked osakesed suurusega alla 10 mikromeetri |  | -
PM2.5 | PM2,5 - tahked osakesed suurusega alla 2,5 mikromeetri | PM2,5 - tahked osakesed suurusega alla 2,5 mikromeetri | PM2,5 - tahked osakesed suurusega alla 2,5 mikromeetri |  | -
TSP | kõik tahked osakesed | kõik tahked osakesed | kõik tahked osakesed |  | Tahked osakesed, summaarsed
Ühikuteisendus: |  |  |  | g/GJ = kg/TJ

## Heited väiksed kütteseadmed EU (hidden)
NFR | Sektor | Table | Type | Tehnoloogia | Kütus | Abatement | Region | Saasteaine | Väärtus | Ühik | CI_lower | CI_upper | Kirjandusallikas
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | BC | 28 | % of PM2.5 | 11 | 39 | Goncalves et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | CO | 2000 | g/GJ | 500 | 5000 | Johansson et al. (2003)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | NH3 | 37 | g/GJ | 18 | 74 | Roe et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | NMVOC | 250 | g/GJ | 20 | 500 | EMEP/EEA Guidebook 2009
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | NOx | 95 | g/GJ | 50 | 150 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | PM10 | 95 | g/GJ | 19 | 238 | Johansson et al.(2003)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | PM2.5 | 93 | g/GJ | 19 | 233 | Johansson et al.(2003)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-42 | Tier 2 emission factor | Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | TSP | 100 | g/GJ | 20 | 250 | Johansson et al.(2003)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-19 | Tier 2 emission factor | Uuemad söepõletustehnikad <1MWth - uuemad ahjud | Kivisüsi / kivisöe tahkekütused |  | NA | BC | 6.4 | % of PM2.5 | 2 | 26 | Zhang et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-19 | Tier 2 emission factor | Uuemad söepõletustehnikad <1MWth - uuemad ahjud | Kivisüsi / kivisöe tahkekütused |  | NA | CO | 2000 | g/GJ | 200 | 3000 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-19 | Tier 2 emission factor | Uuemad söepõletustehnikad <1MWth - uuemad ahjud | Kivisüsi / kivisöe tahkekütused |  | NA | NMVOC | 300 | g/GJ | 20 | 400 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-19 | Tier 2 emission factor | Uuemad söepõletustehnikad <1MWth - uuemad ahjud | Kivisüsi / kivisöe tahkekütused |  | NA | NOx | 150 | g/GJ | 50 | 200 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-19 | Tier 2 emission factor | Uuemad söepõletustehnikad <1MWth - uuemad ahjud | Kivisüsi / kivisöe tahkekütused |  | NA | PM10 | 240 | g/GJ | 76 | 250 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-19 | Tier 2 emission factor | Uuemad söepõletustehnikad <1MWth - uuemad ahjud | Kivisüsi / kivisöe tahkekütused |  | NA | PM2.5 | 220 | g/GJ | 72 | 230 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-19 | Tier 2 emission factor | Uuemad söepõletustehnikad <1MWth - uuemad ahjud | Kivisüsi / kivisöe tahkekütused |  | NA | TSP | 250 | g/GJ | 80 | 260 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | BC | 10 | % of PM2.5 | 2 | 20 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | CO | 4000 | g/GJ | 1000 | 10000 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | NH3 | 70 | g/GJ | 35 | 140 | Roe et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | NMVOC | 600 | g/GJ | 20 | 3000 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | NOx | 50 | g/GJ | 30 | 150 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | PM10 | 760 | g/GJ | 380 | 1520 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | PM2.5 | 740 | g/GJ | 370 | 1480 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-40 | Tier 2 emission factor | Traditsiooniline ahi | Puit ja sarnane puidujääde |  | NA | TSP | 800 | g/GJ | 400 | 1600 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | BC | 16 | % of PM2.5 | 5 | 30 | Kupiainen & Klimont (2007)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | CO | 4000 | g/GJ | 500 | 10000 | Johansson et al. (2003)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | NH3 | 37 | g/GJ | 18 | 74 | Roe et al. (2004) 3)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | NMVOC | 350 | g/GJ | 100 | 2000 | Johansson et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | NOx | 80 | g/GJ | 30 | 150 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | PM10 | 380 | g/GJ | 290 | 760 | Glasius et al. (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | PM2.5 | 370 | g/GJ | 285 | 740 | Glasius et al. (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-41 | Tier 2 emission factor | Energiatõhus ahi | Puit |  | NA | TSP | 400 | g/GJ | 200 | 800 | Glasius et al. (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | BC | 9.839 | % of PM2.5 | 3 | 30 | Engelbrecht et al. (2002)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | CO | 5000 | g/GJ | 3000 | 7000 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | NH3 | 5 | g/GJ | 3 | 7 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | NMVOC | 600 | g/GJ | 360 | 840 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | NOx | 60 | g/GJ | 36 | 84 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | PM10 | 330 | g/GJ | 198 | 462 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | PM2.5 | 330 | g/GJ | 198 | 462 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-12 | Tier 2 emission factor | Kaminad, saunad ja välisoojendid (Outdoor Heaters) | Tahkekütused |  | NA | TSP | 350 | g/GJ | 210 | 490 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-29 | Tier 2 emission factor | Gaasiturbiinid | Kerge kütteõli |  | NA | BC | 33.5 | % of PM2.5 | 20.1 | 46.9 | Hildemann et al. (1991), Bond et al. (2006)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-29 | Tier 2 emission factor | Gaasiturbiinid | Kerge kütteõli |  | NA | CO | 2.6 | g/GJ | 2 | 4 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-29 | Tier 2 emission factor | Gaasiturbiinid | Kerge kütteõli |  | NA | NMVOC | 0.18 | g/GJ | 0.018 | 1.8 | US EPA (2000)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-29 | Tier 2 emission factor | Gaasiturbiinid | Kerge kütteõli |  | NA | NOx | 83 | g/GJ | 50 | 116 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-29 | Tier 2 emission factor | Gaasiturbiinid | Kerge kütteõli |  | NA | PM10 | 9.5 | g/GJ | 6 | 13 | **
1.A.4.b.i | Olme/elamu põletusseade | Table_3-29 | Tier 2 emission factor | Gaasiturbiinid | Kerge kütteõli |  | NA | PM2.5 | 9.5 | g/GJ | 6 | 13 | **
1.A.4.b.i | Olme/elamu põletusseade | Table_3-29 | Tier 2 emission factor | Gaasiturbiinid | Kerge kütteõli |  | NA | TSP | 9.5 | g/GJ | 6 | 13 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-28 | Tier 2 emission factor | Gaasiturbiinid | Maagaas |  | NA | BC | 2.5 | % of PM2.5 | 1.5 | 3.5 | England et al. (2004), Wien et al. (2004), US EPA (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-28 | Tier 2 emission factor | Gaasiturbiinid | Maagaas |  | NA | CO | 4.8 | g/GJ | 1.8 | 42 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-28 | Tier 2 emission factor | Gaasiturbiinid | Maagaas |  | NA | NMVOC | 1.6 | g/GJ | 1 | 2.2 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-28 | Tier 2 emission factor | Gaasiturbiinid | Maagaas |  | NA | NOx | 48 | g/GJ | 29 | 67 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-28 | Tier 2 emission factor | Gaasiturbiinid | Maagaas |  | NA | PM10 | 0.2 | g/GJ | 0.12 | 0.28 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-28 | Tier 2 emission factor | Gaasiturbiinid | Maagaas |  | NA | PM2.5 | 0.2 | g/GJ | 0.12 | 0.28 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-28 | Tier 2 emission factor | Gaasiturbiinid | Maagaas |  | NA | TSP | 0.2 | g/GJ | 0.12 | 0.28 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | BC | 10 | % of PM2.5 | 2 | 20 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | CO | 4000 | g/GJ | 1000 | 10000 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | NH3 | 70 | g/GJ | 35 | 140 | Roe et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | NMVOC | 600 | g/GJ | 20 | 3000 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | NOx | 50 | g/GJ | 30 | 150 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | PM10 | 760 | g/GJ | 380 | 1520 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | PM2.5 | 740 | g/GJ | 370 | 1480 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-6 | Tier 1 emission factor | NA | Biomass |  | NA | TSP | 800 | g/GJ | 400 | 1600 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-4 | Tier 1 emission factor | NA | Gaasilised kütused |  | NA | BC | 5.4 | % of PM2.5 | 2.7 | 11 | Average of Tier 2 EFs for residential gaseous fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-4 | Tier 1 emission factor | NA | Gaasilised kütused |  | NA | CO | 26 | g/GJ | 18 | 42 | Average of Tier 2 EFs for residential gaseous fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-4 | Tier 1 emission factor | NA | Gaasilised kütused |  | NA | NMVOC | 1.9 | g/GJ | 1.1 | 2.6 | Average of Tier 2 EFs for residential gaseous fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-4 | Tier 1 emission factor | NA | Gaasilised kütused |  | NA | NOx | 51 | g/GJ | 31 | 71 | Average of Tier 2 EFs for residential gaseous fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-4 | Tier 1 emission factor | NA | Gaasilised kütused |  | NA | PM10 | 1.2 | g/GJ | 0.7 | 1.7 | Average of Tier 2 EFs for residential gaseous fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-4 | Tier 1 emission factor | NA | Gaasilised kütused |  | NA | PM2.5 | 1.2 | g/GJ | 0.7 | 1.7 | Average of Tier 2 EFs for residential gaseous fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-4 | Tier 1 emission factor | NA | Gaasilised kütused |  | NA | TSP | 1.2 | g/GJ | 0.7 | 1.7 | Average of Tier 2 EFs for residential gaseous fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | BC | 6.4 | % of PM2.5 | 2 | 26 | Zhang et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | CO | 4600 | g/GJ | 3000 | 7000 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | NH3 | 0.3 | g/GJ | 0.1 | 7 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | NMVOC | 484 | g/GJ | 250 | 840 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | NOx | 110 | g/GJ | 36 | 200 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | PM10 | 404 | g/GJ | 76 | 480 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | PM2.5 | 398 | g/GJ | 72 | 480 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-3 | Tier 1 emission factor | NA | Kivisüsi ja pruunsüsi |  | NA | TSP | 444 | g/GJ | 80 | 600 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-5 | Tier 1 emission factor | NA | "Muud" vedelkütused |  | NA | BC | 8.5 | % of PM2.5 | 4.8 | 17 | Average of Tier 2 EFs for residential liquid fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-5 | Tier 1 emission factor | NA | "Muud" vedelkütused |  | NA | CO | 57 | g/GJ | 34 | 80 | Average of Tier 2 EFs for residential liquid fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-5 | Tier 1 emission factor | NA | "Muud" vedelkütused |  | NA | NMVOC | 0.69 | g/GJ | 0.4 | 1 | Average of Tier 2 EFs for residential liquid fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-5 | Tier 1 emission factor | NA | "Muud" vedelkütused |  | NA | NOx | 51 | g/GJ | 31 | 72 | Average of Tier 2 EFs for residential liquid fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-5 | Tier 1 emission factor | NA | "Muud" vedelkütused |  | NA | PM10 | 1.9 | g/GJ | 1.1 | 2.6 | Average of Tier 2 EFs for residential liquid fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-5 | Tier 1 emission factor | NA | "Muud" vedelkütused |  | NA | PM2.5 | 1.9 | g/GJ | 1.1 | 2.6 | Average of Tier 2 EFs for residential liquid fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-5 | Tier 1 emission factor | NA | "Muud" vedelkütused |  | NA | TSP | 1.9 | g/GJ | 1.1 | 2.6 | Average of Tier 2 EFs for residential liquid fuel combustion for all technologies
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | BC | 7 | % of PM2.5 | 2 | 18 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | CO | 4000 | g/GJ | 1000 | 10000 | Goncalves et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | NH3 | 74 | g/GJ | 37 | 148 | Roe et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | NMVOC | 600 | g/GJ | 20 | 3000 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | NOx | 50 | g/GJ | 30 | 150 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | PM10 | 840 | g/GJ | 420 | 1680 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | PM2.5 | 820 | g/GJ | 410 | 1640 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-39 | Tier 2 emission factor | Lahtinde kamin | Puit |  | NA | TSP | 880 | g/GJ | 440 | 1760 | Alves et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | BC | 15 | % of PM2.5 | 6 | 39 | Schmidl et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | CO | 300 | g/GJ | 10 | 2500 | Schmidl et al. (2011) and Johansson et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | NH3 | 12 | g/GJ | 6 | 24 | Roe et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | NMVOC | 10 | g/GJ | 1 | 30 | Johansson et al. (2004) and Boman et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | NOx | 80 | g/GJ | 50 | 200 | Pettersson et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | PM10 | 60 | g/GJ | 30 | 120 | Denier van der Gon et al. (2015)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | PM2.5 | 60 | g/GJ | 30 | 120 | Denier van der Gon et al. (2015)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-44 | Tier 2 emission factor | Pelletahjud ja -boilerid | Puit |  | NA | TSP | 62 | g/GJ | 31 | 124 | Denier van der Gon et al. (2015)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-31 | Tier 2 emission factor | kolbmootor (Reciprocating Engines) | Kerge kütteõli |  | NA | BC | 78 | % of PM2.5 | 47 | 100 | Hernandez et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-31 | Tier 2 emission factor | kolbmootor (Reciprocating Engines) | Kerge kütteõli |  | NA | CO | 130 | g/GJ | 78 | 182 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-31 | Tier 2 emission factor | kolbmootor (Reciprocating Engines) | Kerge kütteõli |  | NA | NMVOC | 50 | g/GJ | 30 | 70 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-31 | Tier 2 emission factor | kolbmootor (Reciprocating Engines) | Kerge kütteõli |  | NA | NOx | 942 | g/GJ | 565 | 1319 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-31 | Tier 2 emission factor | kolbmootor (Reciprocating Engines) | Kerge kütteõli |  | NA | PM10 | 30 | g/GJ | 18 | 42 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-31 | Tier 2 emission factor | kolbmootor (Reciprocating Engines) | Kerge kütteõli |  | NA | PM2.5 | 30 | g/GJ | 18 | 42 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-31 | Tier 2 emission factor | kolbmootor (Reciprocating Engines) | Kerge kütteõli |  | NA | TSP | 30 | g/GJ | 18 | 42 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_04 | Tier 2 emission factor | Elamud - Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | BC | 55 | % of PM2.5 |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.42
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_04 | Tier 2 emission factor | Elamud - Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | PM10 | 49 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.42
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_04 | Tier 2 emission factor | Elamud - Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | PM2.5 | 47 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.42
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_04 | Tier 2 emission factor | Elamud - Uuemad / ökomärgisega ahjud ja boilerid | Puit |  | NA | TSP | 54 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.42
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_05 | Tier 2 emission factor | Elamud - Traditsiooniline boiler < 50 kW | Puit |  | NA | BC | 54 | % of PM2.5 |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.43
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_05 | Tier 2 emission factor | Elamud - Traditsiooniline boiler < 50 kW | Puit |  | NA | PM10 | 150 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.43
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_05 | Tier 2 emission factor | Elamud - Traditsiooniline boiler < 50 kW | Puit |  | NA | PM2.5 | 140 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.43
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_05 | Tier 2 emission factor | Elamud - Traditsiooniline boiler < 50 kW | Puit |  | NA | TSP | 170 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.43
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_02 | Tier 2 emission factor | Elamud - Traditsiooniline ahi | Puit |  | NA | BC | 53 | % of PM2.5 |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.40
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_02 | Tier 2 emission factor | Elamud - Traditsiooniline ahi | Puit |  | NA | PM10 | 160 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.40
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_02 | Tier 2 emission factor | Elamud - Traditsiooniline ahi | Puit |  | NA | PM2.5 | 140 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.40
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_02 | Tier 2 emission factor | Elamud - Traditsiooniline ahi | Puit |  | NA | TSP | 200 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.40
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_03 | Tier 2 emission factor | Elamud - Kõrgefektiivne ahi | Puit |  | NA | BC | 43 | % of PM2.5 |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.41
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_03 | Tier 2 emission factor | Elamud - Kõrgefektiivne ahi | Puit |  | NA | PM10 | 150 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.41
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_03 | Tier 2 emission factor | Elamud - Kõrgefektiivne ahi | Puit |  | NA | PM2.5 | 140 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.41
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_03 | Tier 2 emission factor | Elamud - Kõrgefektiivne ahi | Puit |  | NA | TSP | 170 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.41
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_01 | Tier 2 emission factor | Elamud - Avatud kamin | Puit |  | NA | BC | 24 | % of PM2.5 |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.39
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_01 | Tier 2 emission factor | Elamud - Avatud kamin | Puit |  | NA | PM10 | 260 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.39
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_01 | Tier 2 emission factor | Elamud - Avatud kamin | Puit |  | NA | PM2.5 | 240 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.39
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_01 | Tier 2 emission factor | Elamud - Avatud kamin | Puit |  | NA | TSP | 270 | g/GJ |  |  | Denier van der Gon et al. (2015) applied on EFs in Table 3.39
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_06 | Tier 2 emission factor | Elamud - Pelletahjud ja -boilerid (pelletite põletamine) | Puit |  | NA | BC | 30 | % of PM2.5 |  |  | Denier van der Gon et al. (2015), for BC applied on Schmidl et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_06 | Tier 2 emission factor | Elamud - Pelletahjud ja -boilerid (pelletite põletamine) | Puit |  | NA | PM10 | 30 | g/GJ |  |  | Denier van der Gon et al. (2015), for BC applied on Schmidl et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_06 | Tier 2 emission factor | Elamud - Pelletahjud ja -boilerid (pelletite põletamine) | Puit |  | NA | PM2.5 | 30 | g/GJ |  |  | Denier van der Gon et al. (2015), for BC applied on Schmidl et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-49_06 | Tier 2 emission factor | Elamud - Pelletahjud ja -boilerid (pelletite põletamine) | Puit |  | NA | TSP | 32 | g/GJ |  |  | Denier van der Gon et al. (2015), for BC applied on Schmidl et al. (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-18 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Kerge kütteõli |  | NA | BC | 3.9 | % of PM2.5 | 2 | 8 | US EPA (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-18 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Kerge kütteõli |  | NA | CO | 3.7 | g/GJ | 2 | 5 | Italian Ministry for the Environment (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-18 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Kerge kütteõli |  | NA | NMVOC | 0.17 | g/GJ | 0.06 | 0.51 | Italian Ministry for the Environment (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-18 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Kerge kütteõli |  | NA | NOx | 69 | g/GJ | 41 | 97 | Italian Ministry for the Environment (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-18 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Kerge kütteõli |  | NA | PM10 | 1.5 | g/GJ | 1 | 2 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-18 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Kerge kütteõli |  | NA | PM2.5 | 1.5 | g/GJ | 1 | 2 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-18 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Kerge kütteõli |  | NA | TSP | 1.5 | g/GJ | 1 | 2 | Italian Ministry for the Environment (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-16 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Maagaas |  | NA | BC | 5.4 | % of PM2.5 | 2.7 | 11 | Hildemann et al. (1991), Muhlbaier (1981) **
1.A.4.b.i | Olme/elamu põletusseade | Table_3-16 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Maagaas |  | NA | CO | 22 | g/GJ | 18 | 42 | DGC (2009)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-16 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Maagaas |  | NA | NMVOC | 1.8 | g/GJ | 1.1 | 2.5 | Italian Ministry for the Environment (2005)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-16 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Maagaas |  | NA | NOx | 42 | g/GJ | 25 | 59 | DGC (2009)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-16 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Maagaas |  | NA | PM10 | 0.2 | g/GJ | 0.12 | 0.28 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-16 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Maagaas |  | NA | PM2.5 | 0.2 | g/GJ | 0.12 | 0.28 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-16 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Maagaas |  | NA | TSP | 0.2 | g/GJ | 0.12 | 0.28 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-15 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Tahkekütused |  | NA | BC | 6.4 | % of PM2.5 | 2 | 26 | Zhang et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-15 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Tahkekütused |  | NA | CO | 4787 | g/GJ | 3000 | 7000 | US EPA (1998)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-15 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Tahkekütused |  | NA | NMVOC | 174 | g/GJ | 87 | 260 | US EPA (1998)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-15 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Tahkekütused |  | NA | NOx | 158 | g/GJ | 80 | 300 | US EPA (1998)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-15 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Tahkekütused |  | NA | PM10 | 225 | g/GJ | 113 | 338 | Tivari et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-15 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Tahkekütused |  | NA | PM2.5 | 201 | g/GJ | 100 | 300 | Tivari et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-15 | Tier 2 emission factor | Väikesed (üksikelamu skaalas, võimsus <= 50 kWth) boilerid | Tahkekütused |  | NA | TSP | 261 | g/GJ | 130 | 400 | Tivari et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-30 | Tier 2 emission factor | Statsionaarsed kolbmootorid (reciprocating engines) | Maagaas |  | NA | BC | 2.5 | % of PM2.5 | 1.5 | 3.5 | England et al. (2004), Wien et al. (2004), US EPA (2011)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-30 | Tier 2 emission factor | Statsionaarsed kolbmootorid (reciprocating engines) | Maagaas |  | NA | CO | 56 | g/GJ | 34 | 78 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-30 | Tier 2 emission factor | Statsionaarsed kolbmootorid (reciprocating engines) | Maagaas |  | NA | NMVOC | 89 | g/GJ | 53 | 125 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-30 | Tier 2 emission factor | Statsionaarsed kolbmootorid (reciprocating engines) | Maagaas |  | NA | NOx | 135 | g/GJ | 81 | 189 | Nielsen et al. (2010)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-30 | Tier 2 emission factor | Statsionaarsed kolbmootorid (reciprocating engines) | Maagaas |  | NA | PM10 | 2 | g/GJ | 1 | 3 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-30 | Tier 2 emission factor | Statsionaarsed kolbmootorid (reciprocating engines) | Maagaas |  | NA | PM2.5 | 2 | g/GJ | 1 | 3 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-30 | Tier 2 emission factor | Statsionaarsed kolbmootorid (reciprocating engines) | Maagaas |  | NA | TSP | 2 | g/GJ | 1 | 3 | BUWAL (2001)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-17 | Tier 2 emission factor | Ahjud | Kerge kütteõli |  | NA | BC | 13 | % of PM2.5 | 7.5 | 26 | Bond et al. (2004)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-17 | Tier 2 emission factor | Ahjud | Kerge kütteõli |  | NA | CO | 111 | g/GJ | 67 | 155 | UBA (2008)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-17 | Tier 2 emission factor | Ahjud | Kerge kütteõli |  | NA | NMVOC | 1.2 | g/GJ | 0.7 | 1.7 | UBA (2008)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-17 | Tier 2 emission factor | Ahjud | Kerge kütteõli |  | NA | NOx | 34 | g/GJ | 20 | 48 | UBA (2008)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-17 | Tier 2 emission factor | Ahjud | Kerge kütteõli |  | NA | PM10 | 2.2 | g/GJ | 1.3 | 3.1 | UBA (2008)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-17 | Tier 2 emission factor | Ahjud | Kerge kütteõli |  | NA | PM2.5 | 2.2 | g/GJ | 1.3 | 3.1 | UBA (2008)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-17 | Tier 2 emission factor | Ahjud | Kerge kütteõli |  | NA | TSP | 2.2 | g/GJ | 1.3 | 3.1 | UBA (2008)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-14 | Tier 2 emission factor | Ahjud | Tahkekütused |  | NA | BC | 6.4 | % of PM2.5 | 2 | 26 | Zhang et al. (2012)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-14 | Tier 2 emission factor | Ahjud | Tahkekütused |  | NA | CO | 5000 | g/GJ | 3000 | 7000 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-14 | Tier 2 emission factor | Ahjud | Tahkekütused |  | NA | NMVOC | 600 | g/GJ | 360 | 840 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-14 | Tier 2 emission factor | Ahjud | Tahkekütused |  | NA | NOx | 100 | g/GJ | 60 | 150 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-14 | Tier 2 emission factor | Ahjud | Tahkekütused |  | NA | PM10 | 450 | g/GJ | 228 | 480 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-14 | Tier 2 emission factor | Ahjud | Tahkekütused |  | NA | PM2.5 | 450 | g/GJ | 216 | 480 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-14 | Tier 2 emission factor | Ahjud | Tahkekütused |  | NA | TSP | 500 | g/GJ | 240 | 600 | Guidebook (2006) chapter B216
1.A.4.b.i | Olme/elamu põletusseade | Table_3-13 | Tier 2 emission factor | Ahjud, kaminad, saunad ja välisoojendid (Outdoor Heaters) | Maagaas |  | NA | BC | 5.4 | % of PM2.5 | 2.7 | 11 | Hildemann et al. (1991)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-13 | Tier 2 emission factor | Ahjud, kaminad, saunad ja välisoojendid (Outdoor Heaters) | Maagaas |  | NA | CO | 30 | g/GJ | 18 | 42 | DGC (2009)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-13 | Tier 2 emission factor | Ahjud, kaminad, saunad ja välisoojendid (Outdoor Heaters) | Maagaas |  | NA | NMVOC | 2 | g/GJ | 1.2 | 2.8 | Zhang et al. (2000)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-13 | Tier 2 emission factor | Ahjud, kaminad, saunad ja välisoojendid (Outdoor Heaters) | Maagaas |  | NA | NOx | 60 | g/GJ | 36 | 84 | DGC (2009)
1.A.4.b.i | Olme/elamu põletusseade | Table_3-13 | Tier 2 emission factor | Ahjud, kaminad, saunad ja välisoojendid (Outdoor Heaters) | Maagaas |  | NA | PM10 | 2.2 | g/GJ | 1.3 | 3.1 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-13 | Tier 2 emission factor | Ahjud, kaminad, saunad ja välisoojendid (Outdoor Heaters) | Maagaas |  | NA | PM2.5 | 2.2 | g/GJ | 1.3 | 3.1 | *
1.A.4.b.i | Olme/elamu põletusseade | Table_3-13 | Tier 2 emission factor | Ahjud, kaminad, saunad ja välisoojendid (Outdoor Heaters) | Maagaas |  | NA | TSP | 2.2 | g/GJ | 1.3 | 3.1 | Zhang et al. (2000)
Allikas: | http://efdb.apps.eea.europa.eu/?source=%7B%22query%22%3A%7B%22bool%22%3A%7B%22must%22%3A%7B%22match_all%22%3A%7B%7D%7D%2C%22filter%22%3A%7B%22bool%22%3A%7B%22must%22%3A%5B%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22code%22%3A%221.A.4.b.i%20Residential%20plants%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Pollutant%22%3A%22BC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CH4%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22CO2%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22N2O%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NH3%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NMVOC%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22NOx%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM10%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22PM2.5%22%7D%7D%2C%7B%22term%22%3A%7B%22Pollutant%22%3A%22TSP%22%7D%7D%5D%7D%7D%2C%7B%22bool%22%3A%7B%22should%22%3A%5B%7B%22term%22%3A%7B%22Fuel%22%3A%22%27Other%27%20Liquid%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Biomass%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Coal%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gas%20Oil%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Gaseous%20Fuels%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Hard%20Coal%20and%20Brown%20Coal%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Natural%20Gas%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Solid%20Fuel%20(not%20biomass)%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%22%7D%7D%2C%7B%22term%22%3A%7B%22Fuel%22%3A%22Wood%20and%20similar%20wood%20waste%22%7D%7D%5D%7D%7D%5D%7D%7D%7D%7D%2C%22display_type%22%3A%22tabular%22%7D
Lühendid põlemisel tekkivate lenduvate saasteainete kohta:
BC | must süsinik, mõõdetakse % PM2.5 suhtes | must süsinik, mõõdetakse % PM2.5 suhtes | must süsinik, mõõdetakse % PM2.5 suhtes
CO | CO - süsnikmonooksiid | CO - süsnikmonooksiid | CO - süsnikmonooksiid
NH3 | NH3 - ammoniaak | NH3 - ammoniaak | NH3 - ammoniaak
NMVOC | lenduvad orgaanilised ained v.a. metaan | lenduvad orgaanilised ained v.a. metaan | lenduvad orgaanilised ained v.a. metaan
NOx | NOx - lämmastiku oksiidid | NOx - lämmastiku oksiidid | NOx - lämmastiku oksiidid
PM10 | PM10 - tahked osakesed suurusega alla 10 mikromeetri | PM10 - tahked osakesed suurusega alla 10 mikromeetri | PM10 - tahked osakesed suurusega alla 10 mikromeetri
PM2.5 | PM2,5 - tahked osakesed suurusega alla 2,5 mikromeetri | PM2,5 - tahked osakesed suurusega alla 2,5 mikromeetri | PM2,5 - tahked osakesed suurusega alla 2,5 mikromeetri
TSP | kõik tahked osakesed | kõik tahked osakesed | kõik tahked osakesed
Ühikuteisendus: |  |  |  | g/GJ = kg/TJ

## Kütteväärtused CO2 CH4 N2O EU (hidden)
Allikas: | GREENHOUSE GAS EMISSIONS IN ESTONIA 1990-2019 NATIONAL INVENTORY REPORT | [6 empty] | https://unfccc.int/sites/default/files/resource/est-2021-nir-15apr21_0.zip
Tabelid: 3.9 lk 84-85 ja 3.10 lk 86-87, 3.11-3.13 lk 87 - suurenergeetika ja siin lehel all lõpus tabel 3.33 lk 119 ja osa tabelist Table1.A(a)s4 - kodumajapidamised | [7 empty] | https://unfccc.int/ghg-inventories-annex-i-parties/2020
Table 3.9. Carbon emission factors, oxidation factors and net calorific values by fuels for 2019 | [6 empty] | Table 3.10. CH4 and N2O emission factors by fuel, kg/TJ
Fuels | NCV | Unit | CEF, tC/TJ | Oxidation factor | Source of emission factor |  | Fuels | Energy Industry |  | Manufacturing Industry |  | Source |  | KIK märkus: 2026. aastal avaldatud "GREENHOUSE GAS EMISSIONS IN ESTONIA 1990-2024 NATIONAL INVENTORY DOCUMENT" aruandes kütteväärtused ei erine oluliselt siintoodud väärtustest, mistõttu neid käesolevas tabelis ei uuendata.
| average | [6 empty] | CH4 | N2O | CH4 | N2O
Liquid fuels | [6 empty] | Liquid fuels
LPG | 45.5 | GJ/t | 17.73 | 1 | CS (Estonia) |  | LPG (Liquefied Petrol Gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006
Gasoline (for non-road transport) | 44 | GJ/t | 19.09 | 1 | CS (Estonia) |  | Gasoline | 3 | 0.6 | 3 | 0.6 | D, IPCC 2006
Light fuel oil | 42.5 | GJ/t | 20.26 | 1 | CS (Estonia) |  | Gasoil (light fuel oil) | 3 | 0.6 | 3 | 0.6 | D, IPCC 2006
Shale oil (heavy fraction) | 39.22 | GJ/t | 21.1 | 1 | CS, MoE 2017 |  | Gasoil (for non-road use) | 3 | 0.6 | 3 | 0.6 | D, IPCC 2006
Shale oil (light fraction) | 42.3 | GJ/t | 20.2 | 1 | CS (Estonia), MoE 2017 |  | Shale oil | 3 | 0.6 | 3 | 0.6 | D, IPCC 2006
Diesel oil | 42.3 | GJ/t | 19.87 | 1 | CS (Estonia) |  | Diesel oil | 3 | 0.6 | 3 | 0.6 | D, IPCC 2006
Residual fuel oil (heavy fuel oil) | 40.15 | GJ/t | 20.92 | 1 | CS (Estonia) |  | Residual fuel oil (heavy fuel oil) | 3 | 0.6 | 3 | 0.6 | D, IPCC 2006
Solid fuels | [6 empty] | Recycled waste oil | 30 | 0.6 | 30 | 0.6 | D, IPCC 2006
Coal | 22 | GJ/t | 25.74 | 1 | CS (Estonia) |  | Solid fuels
Coke oven coke | 28.5 | GJ/t | 29.02 | 1 | CS (Estonia) |  | Coal | 1 | 1.5 | 10 | 1.5 | D, IPCC 2006
Oil shale CFB (fludised bed combustion) | 8.16 | GJ/t | 26,42 – | 1 | PS (Estonia) |  | Coke oven coke |  |  | 10 | 1.5 | D, IPCC 2006
|  |  | 27.25 |  |  |  | Oil shale PC12 | 0 | 0 | 10 | 1.5 | CS, A.Ots/ D, IPCC
Oil shale PC (pulverised combustion) | 7.47 | GJ/t | 27,76 – | 1 | PS (Estonia) | [5 empty] | 1.5 | 2006
|  |  | 29.14 |  |  |  | Oil shale FBC* | 0 | 0.82 | 10 | 1.5 | CS, EE/ D, IPCC 2006
Milled peat | 9.7 | GJ/t | 28.9 | 1 | D, IPCC 2006 |  | Milled peat | 1 | 1.5 | 2 | 1.5 | D, IPCC 2006
Sod peat1 | 12 | GJ/t | 27.82 | 1 | FI (Finland) |  | Sod peat | 1 | 1.5 | 2 | 1.5 | D, IPCC 2006
Peat briquette | 16 | GJ/t | 26.45 | 1 | FI (Finland) |  | Peat briquette | 1 | 1.5 | 2 | 1.5 | D, IPCC 2006
Oil shale semi-coke gas (SHC technology, Narva Enefit 140 plant) | 54.59 | GJ/1000 m3 | 18.9 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Oil shale semi-coke gas (SHC technology, Narva Enefit 280 plant) | 46.12 | GJ/1000 m3 | 19.52 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Oil shale semi-coke gas (VKG Petroter I plant) | 43.96 | GJ/1000 m3 | 18.44 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Oil shale semi-coke gas (VKG Petroter | 43.96 | GJ/1000 m3 | 18.44 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
II plant) | [6 empty] | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Oil shale generators gas (VKG Petroter | 43.96 | GJ/1000 m3 | 18.44 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
III plant) | [6 empty] | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Oil shale semi-coke gas (Kiviõli plant) | 49.33 | GJ/1000 m3 | 17.94 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Oil shale generator gas (Kiviõli plant) | 4.24 | GJ/1000 m3 | 38.99 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Oil shale generator gas (VKG plant) | 3.4 | GJ/1000 m3 | 42.61 | 1 | PS (Estonia) |  | Oil shale gases (semi-coke gas and generator gas) | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006 (of natural gas)
Gas gasoline | 44 | GJ/t | 19.09 | 1 | CS (Estonia) |  | Gasoline | 3 | 0.6 | 3 | 0.6 | D, IPCC 2006
Waste oils (CRF 1A2f)* | 16 | GJ/t | 20.18 |  | PS, Kunda Nordic Cement |  | Waste oils |  |  | 30 | 4
Other fossil based solid waste (MSW) (CRF 1A2f) | 19.3 | GJ/t | 21.82 | 1 | PS, Kunda Nordic Cement |  | Other fossil based waste (MSW) |  |  | 30 | 4 | D, IPCC 2006
Plastic waste (CRF 1A2f) | 21.12 | GJ/t | 20.45 | 1 | PS, Kunda Nordic Cement |  | Plastic waste |  |  | 30 | 4 | D, IPCC 2006
Municipal solid waste (CRF 1A1a) | 9 | GJ/t | 17.94 | 1 | PS, Iru incineration plant |  | Municipal solid waste | 30 | 4
Gaseous fuels | [6 empty] | Gaseous fuels
Natural gas | 33.6 | GJ/1000 m3 | 15.07 | 1 | CS (Estonia) |  | Natural gas | 1 | 0.1 | 1 | 0.1 | D, IPCC 2006
Biomass fuels | [6 empty] | Biomass fuels
Solid biomass (solid, includes e.g. firewood, wood chips, sawdust pellets, briquettes, etc.) | 6,9 – 16,9 | GJ/t | 30.5 | 1 | D, IPCC 2006 |  | Solid biomass (solid, includes e.g. firewood, bark, chips, sawdust and other industrial wood residues, pellets and briquettes) | 30 | 4 | 30 | 4 | D, IPCC 2006
Black liquor | 13.4 | GJ/t | 26 | 1 | D, IPCC 2006 |  | Black liquors | 3 | 2 |  |  | D, IPCC 2006
Biogas (landfill gas and biogas from wastewater treatment ) | 17.4 | GJ/1000 m3 | 14.89 | 1 | D, IPCC 2006 |  | Biogas (landfill gas and biogas from wastewater treatment ) | 1.75 | 0.11 |  |  | CS
Lühedid ja märked: | GJ/1000 m3 = MJ/ m3 | [7 empty] | Pöördtabel - Table 3.11. NOx emission factors from Fuel combustion (kg/TJ)
NCV - net calorific value, CEF - Carbon emission factor | [10 empty] | Energy industries | Manufacturing and construction | Other sectors
1 A processed form of peat that is compressed into small (40–70 mm) pieces. | [8 empty] | Coal |  | 200 | 173 | 200
D - IPCC default value; CS – country specific; PS – plant specific *biogenic and non-biogenic origin | [8 empty] | Natural Gas |  | 100 | 60 | 60
[9 empty] | Heavy Fuel Oil |  | 250 | 513 | 51
Table 3.11. NOx emission factors from Fuel combustion (kg/TJ) | [8 empty] | Gas Oil |  | 513
| Coal | Natural Gas | Heavy Fuel Oil | Gas Oil | Biomass | Oil Shale | Peat |  | Biomass |  | 100 | 100 | 100
[9 empty] | Oil Shale |  | 79.02 | 110 | 110
Energy industries | 200 | 100 | 250 | 513 | 100 | 79.02 | 300 |  | Peat |  | 300 | 300 | 300
Manufacturing and construction | 173 | 60 | 513 |  | 100 | 110 | 300
Other sectors | 200 | 60 | 51 |  | 100 | 110 | 300 |  | Pöördtabel - Table 3.12. CO emission factors from Fuel combustion (kg/TJ)
[11 empty] | Energy industries | Manufacturing and construction | Other sectors
Table 3.12. CO emission factors from Fuel combustion (kg/TJ) | [8 empty] | Coal |  | 100 | 931 | 5000
| Coal | Natural Gas | Heavy Fuel Oil | Gas Oil | Biomass | Oil Shale | Peat |  | Natural Gas |  | 40 | 50 | 26
[9 empty] | Heavy Fuel Oil |  | 100 | 66 | 57
Energy industries | 100 | 40 | 100 | 100 | 200 | 0.88 | 100 |  | Gas Oil |  | 100
Manufacturing and construction | 931 | 50 | 66 |  | 700 | 87 | 650 |  | Biomass |  | 200 | 700 | 5009
Other sectors | 5000 | 26 | 57 |  | 5009 | 5000 | 5000 |  | Oil Shale |  | 0.88 | 87 | 5000
[9 empty] | Peat |  | 100 | 650 | 5000
Table 3.13. NMVOC emission factors from Fuel combustion (kg/TJ)
| Coal | Natural Gas | Heavy | Gas Oil | Biomass | Oil Shale | Peat |  | Pöördtabel - Table 3.13. NMVOC emission factors from Fuel combustion (kg/TJ)
|  |  | Fuel Oil | [7 empty] | Energy industries | Manufacturing and construction | Other sectors
Energy industries | 1.5 | 2.5 | 3 | 1.5 | 48 | 0 | 100 |  | Coal |  | 1.5 | 88.8 | 600
Manufacturing and construction | 88.8 | 2.5 | 25 |  | 48 | 60 | 100 |  | Natural Gas |  | 2.5 | 2.5 | 1.9
Other sectors | 600 | 1.9 | 0.69 |  | 271.58 | 600 | 600 |  | Heavy Fuel Oil |  | 3 | 25 | 0.69
[9 empty] | Gas Oil |  | 1.5
[9 empty] | Biomass |  | 48 | 48 | 271.58
[9 empty] | Oil Shale |  | 0 | 60 | 600
NMVOC - lenduvad orgaanilised ühedid, mis pole metaan | [8 empty] | Peat |  | 100 | 100 | 600
The GHGs covered are carbon dioxide (CO2), methane (CH4), nitrous oxide (N2O), nitrogen trifluoride (NF3), hydrofluorocarbons (HFCs), perfluorocarbons (PFCs) and sulphur hexafluoride (SF6). Emission estimates for nitrogen oxides (NOx), carbon monoxide (CO), nonmethane volatile organic compounds (NMVOCs) and sulphur dioxide (SO2) are also included in the inventory.
lk 51.
3.2.6. | Other sectors (CRF 1.A.4) |  |  | 1.A.4.b Residential (Households) |  |  | Antud andmeid kasutatud, kui Table 3.33 vastavat väärtust pole
Table 3.33. CH4 and N2O emission factors for small combustion of fuels, kg/TJ | [5 empty] | lk 119 | Table1.A(a)s4 | https://unfccc.int/ghg-inventories-annex-i-parties/2020 | Vastavatest andmetest valida Estonia, CRF ja tabelid alla laadida. Võtta viimase, 2020 aasta sõidukite andmed, tabelid Table1A(a)s4, veerg D-F, read23-29.
| CH4 | N2O | Source |  |  |  | GREENHOUSE GAS SOURCE AND SINK CATEGORIES | IMPLIED EMISSION FACTORS
Oil | 10 | 0.6 | 2006 IPCC |  |  |  |  | CO2(1) | CH4 | N2O
LPG | 5 | 0.1 | 2006 IPCC
Natural gas | 5 | 0.1 | 2006 IPCC |  |  |  |  | (t/TJ) | (kg/TJ) | (kg/TJ)
Coal (commercial) | 10 | 1.5 | 2006 IPCC |  |  |  | b. Residential(13)
Coal (residential, agriculture) | 300 | 1.5 | 2006 IPCC |  |  |  | Liquid fuels | 67.0404 | 6.09 | 0.209
Oil shale (commercial) | 10 | 1.5 | 2006 IPCC |  |  |  | Solid fuels | 94.3979 | 300 | 1.5
Oil shale | 300 | 1.5 | 2006 IPCC |  |  |  | Gaseous fuels | 55.2567 | 5 | 0.1
Peat/peat briquette (commercial) | 10 | 1.4 | 2006 IPCC |  |  |  | Other fossil fuels(4) | NO | NO | NO
Peat/peat briquette (residential, agriculture) | 300 | 1.4 | 2006 IPCC |  |  |  | Peat(5) | NO | NO | NO
Wood | 300 | 4 | 2006 IPCC |  |  |  | Biomass(6) | 112 | 300 | 4

## Kütteväärtused EE (hidden)
Majandus- ja kommunikatsiooniministri |  |  |  |  | Ümberarvutus:
| 8. oktoobri 2012. a määrus nr 63 |  |  |  | 1Wh=3,6kJ | 3.6
| „Hoonete energiatõhususe arvutamise metoodika” |  |  |  | 1kWh=3600kJ=3,6MJ
Lisa 4
Kütuste tarbimisaine alumised kütteväärtused
Kütus | Alumine kütteväärtus
| kWh/kg | kWh/l | kWh/m3 | MJ/kg | MJ/l | MJ/m3
Põlevkiviõli | 10.8 | 10 |  | 38.88 | 36
Kerge kütteõli | 11.7 | 10 |  | 42.12 | 36
Diislikütus | 11.7 | 9.7 |  | 42.12 | 34.92
Masuut | 11.3 | 10.9 |  | 40.68 | 39.24
Maagaas |  |  | 9.3 |  |  | 33.48
Vedelgaas (propaan + butaan) | 12.8 |  |  | 46.08
Biogaas1 |  |  | 6 |  |  | 21.6
Halupuit (niiskussisaldus2 ≤20%) | 4.1 |  |  | 14.76
Küttepuud, segapuit (ruumimeeter) |  |  | 1300 |  |  | 4680
Küttepuud, kask (ruumimeeter) |  |  | 1500 |  |  | 5400
Puiduhake (puistekuupmeeter) |  |  | 800 |  |  | 2880
Puitbrikett (niiskussisaldus2 ≤12%) | 4.6 |  |  | 16.56
Puitpellet (niiskussisaldus2 ≤12%) | 4.6 |  |  | 16.56
Turbabrikett (niiskussisaldus2 ≤20%) | 4.2 |  |  | 15.12
Tükkturvas (niiskussisaldus2 ≤40%) | 3.4 |  |  | 12.24
Freesturvas (niiskussisaldus2 ≤50%) | 2.8 |  |  | 10.08
Kivisüsi | 7 |  |  | 25.2
1 ligikaudne väärtus, tegelik väärtus kõigub sõltuvalt toormest
2 niiskussisaldused massiprotsentides

## puidu arvutused (hidden)
Küttepuud (cerbos.ee)
Küttepuude kütteväärtus
Kütteväärtus on soojushulk, mis eraldub puidu põlemisel. Erinevatel puuliikidel on erinev kütteväärtus. Enamlevinud küttepuude keskmised kütteväärtused 20% puiduniiskuse juures ("Puitkütus" 2010, SA Erametsakeskus):
kask 1700 kWh/rm
mänd 1360 kWh/rm
haab 1330 kWh/rm
kuusk 1320 kWh/rm
lepp 1230 kWh/rm
Küttepuude koguse mõõtmine
Küttepuude tellimisel on oluline aru saada erinevatest kasutuselolevatest mõõtühikutest ja nendevahelistest seostest:
Tihumeeter (tm) on 1 m3 puhta puidu maht ilma koore ja õhuvahedeta (1 m × 1 m × 1 m).
Ruumimeeter (rm) on 1 m3 virna/riita laotud halgudelt mõõdetud metsamaterjali kogus koos koore ja õhuvahedega.
Puisteruum on ebakorrapäraselt kuhjatud halud koos koore ja õhuvahedega.
Järgnev tabel aitab paremini mõista seoseid mõõtühikute vahel
TREA ettekanne, slaid 27 (allikas Wood Fuels…, 2000)
| Küttepuud (cerbos.ee) |  |  | https://www.trea.ee/ettekanded/UloKaskspets_loeng_1_18_04_2017.pdf
| Puisteruum | Laotud ruum e ruumimeeter | Tihumeeter |  | Puisteruum | Laotud ruum e ruumimeeter | Tihumeeter
Puisteruum | 1 | 0.67 | 0.44 | Puisteruum | 1 | 0.6 | 0.4
Laotud ruum e ruumimeeter | 1.5 | 1 | 0.67 | Laotud ruum e ruumimeeter | 1.68 | 1 | 0.67
Tihumeeter | 2.25 | 1.5 | 1 | Tihumeeter | 2.5 | 1.49 | 1
Puisteruum - puud koos õhuvahedega (ca 46% puitu ja 54% õhuvahed). | [5 empty] | slaid 40
Laotud ruum - puud koos õhuvahedega (ca 69% puitu ja 31% õhuvahed).
Tihumeeter - puud ilma õhuvahedeta (ca 100% puitu õhuvahedeta).
Tavapraktikas korrutatakse ruumimeetrid koefitsiendiga 0,5-0,6, et saada puidu mahtu tihumeetrites. Alati on oluline pöörata tähelepanu, kas müüja poolt pakutav hind kehtib tihumeetri, riidaruumi või puisteruumi kohta. Juhul kui osta kolme meetri pikkuseid saagimata ja lõhkumata küttepuid, moodustavad õhuvahed virnas olevate puude puhul keskmiselt 50% ehk 1 tihumeeter
Küttepuude erikaal
Kuivade küttepuude kaal on märgadega võrreldes tunduvalt väiksem. Küttepuu kuivab peaaegu kaks korda kokku. Tihe küttepuu annab kütmisel rohkem soojust.
Kaal 20% niiskuse juures:
- 1 ruumimeeter (rm) kasehalge kaalub u 480 kg
- 1 rm kuusehalge kaalub u 330 kg
- 1 rm lepahalge kaalub u 400 kg
Keskmine ruumimeetri kaal | 403.3333 | kg/rm
Kask ruumimeetri kaal | 330 | kg/rm
Puistekuupmeetri kaal | 268.8889 | kg/pk
Puiduhakke puistekuupmeetri kaal | 325 | kg/rm

## Elekter 2025 (hidden)
Eesti 2025. a elektri segajäägi CO2 sisaldus.
Segajääk väljendab elektrienergia päritolu, kui see ei ole tõendatud päritolutunnistustega |  |  |  |  | Andmeallikas: | https://www.elextra.ee/segajaak
g/kWh
CO2 | 467.35
N2O | NA |  | * Elering ega AIB ei avalikusta segajäägi CH4 ja N2O komponenti
CH4 | NA
Andmed lahtrites, mis puudutavad erinevatest taastumatutest lähteainetsest elektri tootmist Eestis, on Eesti Keskkonnauuringute Keskuse poolt antud 2020. aasta EL heitkogustega kauplemissüseemi (European Union Emission Trading Scheme) aruandluse andmed. Andmed ei ole avalikult viidatavad.
Kasvuhoonegaaside eriheited (sinised numbrid) on saadud dokumentidest Greenhouse gas emissions in Estonia 1990-2020. National inventory report.” Lk. 79-80 “Table 3.9. Carbon emission factors, oxidation factors and net calorific values by fuels for 2020” ja lk. 81-82 “CH4 and N2O emission factors by fuel, kg/TJ”. Süsiniku eriheide on tC/TJ CO2 arvutamiseks ja CH4 ning N2O puhul on kg/TJ. Samad andmed ka Estonia 1990-2020. National inventory report.”
Taastuvenergia abil toodetud elektri andmed on pärit Eesti Taastuvenergia koja aastaraamatust 2020 lk 15. 2021 aasta andmed on pärit stastistikaametist. | [7 empty] | ETEK_aastaraamat_2020_veebi (taastuvenergeetika.ee)
KE033: ELEKTRIJAAMADE TOODANG JA ENERGIA TOOTMISEKS TARBITUD KÜTUS. Statistika andmebaas
|  | 2020 | 2021 | [5 empty] | Allikas: statistikaamet | https://andmed.stat.ee/et/stat/majandus__energeetika__energia-tarbimine-ja-tootmine__aastastatistika/KE033/table/tableViewLayout2
Oil ShalePC (pulverised combustion) | TJ | 4527.8918 | TJ | 12888.0086 | GWh | 3579 | [6 empty] | Teisendus
| Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 |  |  |  |  | 2021 |  | TJ = | =GWh
CO2 | 29.453 | 488.9861 | 29.453 | 1391.8304 | 106.0604 | 1391.8304 |  |  |  |  | Kõik elektrijaamad |  | 1 | 0.2777
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O |  |  | Kokku | Toodetud elektrienergia, GWh | 7359 |  | 26499.8199 | 7359
CH4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Elektrienergia tootmiseks tarbitud kütus | ..
N2O | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Kivisüsi, tuhat t | Toodetud elektrienergia, GWh | ..
t CO2 eq |  | 488.9861 |  | 1391.8304 |  | 1391.8304 |  |  |  | Elektrienergia tootmiseks tarbitud kütus | ..
[9 empty] | Põlevkivi, tuhat t | Toodetud elektrienergia, GWh | 3579
Oil Shale FBC (fludised bed combustion) | TJ | 17686.3782 | [7 empty] | Elektrienergia tootmiseks tarbitud kütus | 4357
| Carbon Emission Factor, tC/TJ | heide, t CO2 | [6 empty] | Turvas, tuhat t | Toodetud elektrienergia, GWh | ..
CO2 | 27.4068 | 1777.3326 | [7 empty] | Elektrienergia tootmiseks tarbitud kütus | ..
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | [6 empty] | Puiduhake ja -jäätmed, tuhat tm | Toodetud elektrienergia, GWh | 1694
CH4 | 0 | 0 | [7 empty] | Elektrienergia tootmiseks tarbitud kütus | 1512
N2O | 0.82 | 0.014503 | [6 empty] | Raske kütteõli, tuhat t | Toodetud elektrienergia, GWh | ..
t CO2 eq |  | 1781.6544 | [7 empty] | Elektrienergia tootmiseks tarbitud kütus | ..
[9 empty] | Põlevkivikütteõli (raske fraktsioon), tuhat t | Toodetud elektrienergia, GWh | 37
Milled Peat | TJ | 28.224 |  |  |  | 0 |  |  |  | Elektrienergia tootmiseks tarbitud kütus | 11
| Carbon Emission Factor, tC/TJ | heide, t CO2 | [6 empty] | Diislikütus, tuhat t | Toodetud elektrienergia, GWh | ..
CO2 | 28.9 | 2.9886 | [7 empty] | Elektrienergia tootmiseks tarbitud kütus | ..
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | [6 empty] | Maagaas, mln m³ | Toodetud elektrienergia, GWh | 42
CH4 | 1.3813 | 3.8985e-05 | [7 empty] | Elektrienergia tootmiseks tarbitud kütus | 6
N2O | 2.004 | 5.656e-05 | [6 empty] | Biogaasid, mln m³ | Toodetud elektrienergia, GWh | 15
CO2 eq |  | 3.0065 | [7 empty] | Elektrienergia tootmiseks tarbitud kütus | 4
[9 empty] | Jäätmekütus, tuhat t | Toodetud elektrienergia, GWh | 151
BIOMASS | [9 empty] | Elektrienergia tootmiseks tarbitud kütus | 57
Solid Biomass | [8 empty] | Muud taastuvad allikad, TJ | Toodetud elektrienergia, GWh | 20
Wood and wood waste | TJ | 11294 | TJ | 6100.108 | GWh | 1694 |  |  |  | Elektrienergia tootmiseks tarbitud kütus | 123
| Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 |  |  | Põlevkivigaas, TJ | Toodetud elektrienergia, GWh | 711
CO2 wood | 0 |  | 0 |  | 0 | 0 |  |  |  | Elektrienergia tootmiseks tarbitud kütus | 8253
CO2 Black liqour | 0 |  | 0 | [5 empty] | Hüdroenergia | Toodetud elektrienergia, GWh | 23
CO2 | [9 empty] | Elektrienergia tootmiseks tarbitud kütus | ..
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O |  |  | Tuuleenergia | Toodetud elektrienergia, GWh | 733
CH4 Solid | 14.9284 | 0.1686 | 14.9284 | 0.091065 | 53.7572 | 0.091065 |  |  |  | Elektrienergia tootmiseks tarbitud kütus | ..
Total CH4 |  | 0.1686 |  | 0.091065 | 0 | 0.091065 |  |  | Päikeseenergia | Toodetud elektrienergia, GWh | 354
N2OSolid | 2.078 | 0.023469 | 2.078 | 0.012676 | 7.483 | 0.012676 |  |  |  | Elektrienergia tootmiseks tarbitud kütus | ..
Total N2O |  | 0.023469 |  | 0.012676 |  | 0.012676
CO2 eq |  | 11.2089 |  | 6.0541 |  | 6.0541 |  |  | Allikas Elering | https://elering.ee/segajaak
Segajääk 2019-2022
Natural Gas | TJ | 94.9641 | TJ | 151.2423 | GWh | 42 |  |  | Aasta | Tõendamata päritoluga elektri osakaal | Taastuv (RES) | Fossiilne (FOS) | Tuuma (NUC) | CO2 (g/kWh) | Radioaktiivsed jäätmed (mg/kWh)
| Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 |  |  | 2019 | 95.09% | 1.48% | 81.79% | 16.73% | 757.71 | 0.51
CO2 | 15.07 | 5.2436 | 15.07 | 8.3511 | 54.2672 | 8.3511 |  |  | 2020 | 89.91% | 6.6% | 69.47% | 23.93% | 546.89 | 0.88
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O |  |  | 2021 | 85.14% | 7.55% | 76.37% | 16.08% | 636.58 | 0.65
CH4 | 1.0008 | 9.5038e-05 | 1.0008 | 0.00015136 | 3.6038 | 0.00015136 |  |  | 2022 | 84.1% | 7.22% | 83.11% | 9.67% | 715.18 | 0.36
N2O | 0.13704 | 1.3014e-05 | 0.13704 | 2.0727e-05 | 0.49349 | 2.0727e-05 |  |  | 2022.a. on Eestis päritolutunnistustega katmata elektrienergia tarbimise osakaal 84,10%, segajäägi CO2 sisaldus on 715,18 gCO2/kWh ning radioaktiivsete jäätmete sisaldus 0,36 mg/kWh.
CO2 eq |  | 5.2498 |  | 8.361 |  | 8.361
Shale Oil (Heavy fraction) | TJ | 220.5625 | TJ | 133.2373 | GWh | 37 |  |  | Allikas Statistikaamet: |  | https://andmed.stat.ee/et/stat/majandus__energeetika__energia-tehususe-naitajad/KE36/table/tableViewLayout2
| Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 |  |  |  | 2020 | 2021
CO2 | 20.7403 | 16.7611 | 20.7403 | 10.125 | 74.686 | 10.125 |  |  | Taastuvenergiast toodetud elektri osatähtsus elektri kogutarbimises*, % | 28.3 | 29.3
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O
CH4 | 1.1726 | 0.00025863 | 1.1726 | 0.00015624 | 4.2226 | 0.00015624
N2O | 0.33961 | 7.4905e-05 | 0.33961 | 4.5249e-05 | 1.2229 | 4.5249e-05
CO2 eq |  | 16.7899 |  | 10.1424 |  | 10.1424
Gaseous biomass landfill and SW gas | TJ | 124 | TJ | 54.0151 | GWh | 15
| Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2
CO2 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O
Total CH4 | 0.22197 | 2.7524e-05 | 0.22197 | 1.199e-05 | 0.79932 | 1.199e-05
Total N2O | 0.11514 | 1.4277e-05 | 0.11514 | 6.2193e-06 | 0.41462 | 6.2193e-06
CO2 eq |  | 0.0049428 |  | 0.0021531 |  | 0.0021531
Municipal Wastes | t | 121169.5 |  | 57000 |  | 57000
| TJ | 1198.3664 | TJ | 543.7523 | GWh | 151
| Carbon Emission Factor, tC/T | heide, t CO2 | Carbon Emission Factor, tC/T | heide, t CO2 | Carbon Emission Factor, tC/T | heide, t CO2
CO2 | 0.592 | 71.7323 | 0.592 | 33.744 | 0.592 | 33.744
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O
Total CH4 | 0.0038955 | 4.6683e-06 | 0.0038955 | 2.1182e-06 | 0.014028 | 2.1182e-06
Total N2O | 0.17532 | 0.00021009 | 0.17532 | 9.5329e-05 | 0.63132 | 9.5329e-05
CO2 eq |  | 71.7951 |  | 33.7725 |  | 33.7725
Oil Shale Gas | TJ | 12883.8231 | TJ | 2560.3169 | GWh | 711
| Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2 | Carbon Emission Factor, tC/TJ | heide, t CO2
CO2 |  | 1131.353 |  | 224.8263 |  | 224.8263
| CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O | CH4 and N2O emission factors by fuel, kg/TJ | heide, t CH4 või N2O
CH4 | 1 | 0.012884 | 1 | 0.0025603 | 3.601 | 0.0025603
N2O | 0.1 | 0.0012884 | 0.1 | 0.00025603 | 0.3601 | 0.00025603
CO2 eq |  | 1132.059 |  | 224.9666 |  | 224.9666
Tuul | TJ | 2966.1627 | TJ | 2639.5391 | GWh | 733
Päike | TJ | 428.3657 | TJ | 1274.7569 | GWh | 354
Hüdro | TJ | 97.1922 | TJ | 82.8232 | GWh | 23
Muud taastuvad allikad | TJ |  | TJ | 72.0202 | GWh | 20
6.7735
Teisendusfaktor TJ > GWh | 0.2778
Teisendusfaktor GWh > TJ | 3.5997
Toodetud elekter |  | 2020(*) |  |  |  | 2021(***)
Tuul | GWh | 824 |  |  | GWh | 733
Päike | GWh | 119 |  |  | GWh | 354
Biomass(**) | GWh | 1226 |  |  | GWh | 1694
Biogaas(**) | GWh | 29 |  |  | GWh | 15
Hüdro | GWh | 27 |  |  | GWh | 23
Muud taastuvad allikad |  |  |  |  | GWh | 20
| Kokku | 2225 |  |  | Kokku | 2839 | 2577.67
[5 empty] | % | 38.5786 | 35.0274
(*) 2020 andmed | ETEK_aastaraamat_2020_veebi (taastuvenergeetika.ee) |  |  | lk 15
(**) Summaarsete väärtuste saamiseks on kasutatud ülaltoodud ETS andmeid ja topeltarvestuse vältimiseks siinseid samaseid andmeid ei kasutata.
(***) Summaarsete väärtuste saamiseks on kasutatud antud tabelis toodud 2021. aasta andeid
[7 empty] | 2020 |  |  |  | 2021
TOTAL | TJ | 51549.9308 | TJ | 26499.8199 | GWh | 7359 |  | kt/TJ | t/TJ=kg/GJ=g/MJ | kg/TJ=g/GJ |  | kt/TJ | t/TJ=kg/GJ=g/MJ | kg/TJ=g/GJ
TOTAL CO2 | kt | 3494.3973 |  | 1668.8768 |  | 1668.8768 | TOTAL CO2 | 0.067787 | 67.7867 | 67786.654 | TOTAL CO2 | 0.062977 | 62.9769 | 62976.91
TOTAL CH4 | kt | 0.18191 |  | 0.093947 |  | 0.093947 | TOTAL CH4 | 3.5288e-06 | 0.0035288 | 3.5288 | TOTAL CH4 | 3.5452e-06 | 0.0035452 | 3.5452
TOTAL N2O | kt | 0.039629 |  | 0.0131 |  | 0.0131 | TOTAL N2O | 7.6876e-07 | 0.00076876 | 0.76876 | TOTAL N2O | 4.9433e-07 | 0.00049433 | 0.49433
TOTAL CO2 eq. | kt | 3510.7546 |  | 1675.1292 |  | 1675.1292
KONTROLL |  | 3510.7546 |  | 1675.1292 |  | 1675.1292
|  | 0 |  | 0 |  | 0
Elektri eriheide | kt CO2/TJ | 0.067787 |  | 0.062977 |  | 0.22678
Elektri eriheide | kt CO2 eq./TJ | 0.068104 |  | 0.063213 |  | 0.22763
Elektri eriheide | t CO2/TJ | 67.7867 |  | 62.9769 |  | 226.7804
Elektri eriheide | t CO2 eq./TJ | 68.104 |  | 63.2129 |  | 227.63
Eesti elektri brutotootmine | GWh | 5956.5 |  |  |  | 7359
Eesti elektri brutotootmine | TJ | 21441.6847 |  |  |  | 26499.8199
Halli elektri eriheide
Elektri eriheide | kt CO2/GWh | 0.58665 |  |  |  | 0.22678 | kt CO2 eq./GWh | Keskmine taastuvelektri osakaal kogu elektri aastasest tarbimisest.
Elektri eriheide | kt CO2 eq/GWh | 0.5894 |  |  |  | 0.22763 | 0.78587 | 0.25 | 2020. aasta taastuva osakaal 25% |  | ETEK_aastaraamat_2020_veebi (taastuvenergeetika.ee) |  |  |  | lk 15
[7 empty] | 0.63658 | 0.293 | 2020. aasta taastuva osakaal 29,3% |  | https://andmed.stat.ee/et/stat/majandus__energeetika__energia-tehususe-naitajad/KE36/table/tableViewLayout2
Elektrijaamade kasutegur bruto | % | 41.59% |  |  |  |  | 2021. aasta eleringi segajäägi ametlikud andmed |  | https://elering.ee/segajaak
https://andmed.stat.ee/et/stat/majandus__energeetika__energia-tarbimine-ja-tootmine__aastastatistika/KE033/table/tableViewLayout2 | [5 empty] | Valikud: "Vali kõik", "Toodetud elektrienergia, GWh", "2021", "Kõik elektrijaamad"
Tarbimine
2021 |  | Teisendus
845.5281 | kToe | 1 | ktoe
9833.492 | MWh | 11.63 | MWh